## Slide 1
ｚ
Rev. 20231020 1710 PS LV 220ppi
VX-3000 series
Ph.2
v.5.2
INTEGRATED VOICE EVACUATION SYSTEM

## Slide 2
Chart: 
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
 | 5 | 8 | 18 | 1 | 1 | 3 | 2 | 4 | 3 | 3 | 25 | 1 | 3 | 10 | 3 | 18 | 5 | 7
Chart: 
| 26
 | 12
Chart: 
| 29
 | 1
This document has over 100 pages.
You may not need to see everything.
Look at the summary of each section and read as needed.
The numbers attached to the bar graphs are the number of pages.
An overview of this system.
The components and scale of this system.
The functions provided by this system.
Read on to find out what this system can do.
Details of the system and component equipment are introduced for system designers.
Understand how the above functionality is achieved and how the components fit together.
Examples of how the system works.

## Slide 3
The issue of security is more than ever important.
Our VX-3000 is a reliable and energy-saving voice alarm system that combines all important functions for PA/VA in one unit frame. The limited number of components makes the design and installation much easier, as well as saving space and reducing cable complexity. This enables rapid system conﬁguration and makes the VX-3000 a cost effective system.
It comes with low loss modular class D ampliﬁers, with 3 different output ratings. These can easily be removed or replaced simply by unplugging them; there is no need for specialist tools. By using low loss modular class D ampliﬁers and modern power supply switching technology the system becomes much more energy efﬁcient and keeps the operating costs low.
Thanks to its ﬂexible and scalable system architecture the VX-3000 system can be used for both small and large applications, with up to 320 remote microphones and 160 audio sources.
VX-3000 series
Combined highly integrated voice alarm and public address system

## Slide 4
Feature

## Slide 5
More Flexible and Scalable
v.4
adv
Four systems integration is now possible
with v.4 update.
Maximum number of audio inputs: 960
Maximum number of outputs: 2,560 zones
Feature
TOA's VX-3000 Series got certified with EN 50121-4 (IEC62236-4)
the electromagnetic standards which applies to a signaling and telecommunication apparatus installed in railway environment. Those systems can now be utilized in railway applications where EN 50121-4 is required.
EN 50121-4 specifies limits for emission and immunity
and provides performance criteria for signalling and telecommunications apparatus which may interfere
with other apparatus in the railway environment,
or increase the total emissions for the railway
environment beyond the limits defined
in the appropriate standard and so risk
causing electromagnetic interference to
apparatus outside the railway system.
* Not applicable to RM-300X, RM-210F

## Slide 6
Feature
Compact
6in-4bus-4out
19U+8U
Perforated panel x2 2U
VP-2241 x4 8U
Perforated panel 1U
VX-2000 3U
Perforated panel 1U
VX-2000SF 3U
VX-2000PF 3U
Perforated panel 1U
VX-2000DS 2U
Perforated panel 3U
Max 6in-4bus-4out
only 6U+3U
Perforated panel 1U
VX-3000F 3U
Perforated panel 1U
VX-3000DS 3U
Perforated panel 1U
VX-2000
VX-3000
Comparison between VM-3000
Compact
6in-2bus-6out SS
(BGM bus)
6in-1bus-6out SS
& Standby AMP
OR
VM-3000
6in-2bus-8out SS & Standby AMP
(BGM bus)
VX-3000
In small system,
VX-3000 is very compact.
VX-2000 need 19U.
But VX-3000 need only 6U
VM-3000 is not equipped with BGM bus function and AMP redundant together,
but VX-3000 can use both functions.
Comparison between
VX-2000

## Slide 7
Feature
Scalable
VX-2000
In VX-2000
8in, 80out, but only 4bus....
not considered distributed arrangement.
Are amplifiers really necessary for every zones??
Comparison between
VX-2000
*560in = (6in/Frame + 8in/PM) x 40 units.
PM means VX-3000PM, added to the system from v.5.1
Each number has been increased v.2->v.3->v.5.1 as follows.
192->240->560, 512->640->640, 128->160->160,
VX-3000
VX link
VX link
In VX-3000
System total Max *560in, 640out (40unit), 160 broadcasts simultaneously!!
IP based Network connection decentralize system constitution is possible!!
equipped with Speaker selector, possible to design reasonable & efficient system
x 4 system integration
v.5.1
v.4
adv

## Slide 8
Overview
Digital Power Amplifier
VP-3154/3304/3504
Power Supply Manager
VX-3000DS/3150DS
for SX-2000/VX-2000/
VM-3000 series only
Frame
VX-3004F/3008F/3016F
Power Amplifier Module
VX-015DA/030DA/050DA
Remote Microphone
RM-300X, RM-210F
Ph.1
Ph.2
2014
2016
v.2
v.3
2017
By applying firmware ver.5.00 to VX-30##F and setting VX-30##F using setting software ver.5.00, the function of latest version: ver.5.00 is available.
The v.# mark attached to each function introduced in this document
indicates that the functions are available from these versions.
v.4
2018
v.5
2019-
2018
Wall Mount Type
VX-3308WM
Wall mount type based on VX-3008F
Fireman’s
Remote Microphone
RM-200SF, RM-320F
EXISTING
Line Output Module
VX-300LO
Preamp Matrix Panel
VX-3000PM
Control Panel
VX-3000CT
Remote Microphone
RM-500
v.5.2
v.5.1
v.5.1
v.5.1

## Slide 9
Overview
Power Supply Manager
VX-3000DS
Frame
VX-3004F/3008F/3016F
DS link
VX link
(Network)
RS link
Power Amplifier Module
VX-015DA/030DA/050DA
Power Supply Manager
VX-3000DS
Frame
VX-3004F/3008F/3016F
DS link
VX link
(Network)
RS link
Power Amplifier Module
VX-015DA/030DA/050DA
Remote Microphone
RM-300X
Remote Microphone
RM-300X/310F
Fireman’s Microphone
RM-200SF/320F (existing items of SX-2000 series)
The frame is a device as a master constituting a system. Each frame has audio input and output.
The 1st unit set “ID:0” is the manager of the system. Module-type AMP is incorporated in the frame. In the frame interval, it is connected in a IP-based network called “VX link”.
ID:0 frame
System manager
Basic
configuration
Detail
Line Output Module
VX-300LO

## Slide 10
Overview
DS link
RS link
DS link
RS link
Minimum
Distributed arrangement
The system constitution of various scales is possible by the combination of frame and amplifier module. In addition, the construction of the distribute arrangement system is possible because each frames are connected with network connection.
VX link
Basic
configuration
40frames
Max
v.2: 32 frames
Detail
v.3
x 4 system integration
160 frames
v.4
adv

## Slide 11
Overview
Detail
Single output and SS system.
Many zone are connected to 1AMP, Low cost system.
Like the VM style.
Multi-route system.
Each 1 Zone has 1AMP.
Like the SX/VX-2000 style.
AMP
SS
SS
SS
matrix
AMP
AMP
AMP
AMP
matrix
One of the attractive features of VX-3000 is that it is possible to constitute both “The multi-route system like SX/VX” and “The system only branching off an SP line in SS (Speaker Selector) like VM” system.
Basic
configuration

## Slide 12
AMP
AMP
AMP
AMP
matrix
AMP
AMP
AMP
AMP
matrix
AMP
SS
SS
SS
matrix
AMP
AMP
AMP
AMP
matrix
VX link
(Network)
Overview
VX link constitutes the huge free matrix which each flame are connected to.
One of the attractive features of VX-3000 is that it is possible to constitute both “The multi-route system like SX/VX” and “The system only branching off an SP line in SS (Speaker Selector) like VM” system.
Detail
Basic
configuration

## Slide 13
AMP
AMP
AMP
AMP
matrix
AMP
AMP
AMP
AMP
matrix
AMP
SS
SS
SS
matrix
AMP
AMP
AMP
AMP
matrix
VX link
(Network)
Overview
Attractive one of the VX is what can constitute “The multi-route system such as SX/VM” and “The system branching off only an SP line in SS such as VM”.
You can broadcast to the local zones off cause,
not only where, can broadcast the zones connected other Frame via VX link.
Basic
configuration
There is no time difference between frames in broadcasting.
Detail

## Slide 14
Overview
Three units added from v.5.1 have been added.
These are installed in relation to the frame.
However, there are no restrictions from the frame in terms of functionality.
Basic
configuration
Preamp Matrix Panel
VX-3000PM
The PM has two main roles.
One is simply adding an audio input. Each unit has 8 inputs.
There are other benefits aside from the additional input. The VX-3000 originally consisted of a frame with integrated input and output. Although this is compact and convenient, it is wasteful when the input and output sides must be installed separately. PM can be an input-only unit.
1 PM can be installed per frame in 1 system. This means that up to 40 devices/systems can be connected.
Connected with VX link.
Line Out Module
VX-300LO
This is a module for outputting line signals from the frame.
The frame was designed as a device to mount an amplifier and did not have
a line level output. This module
attaches to the frame in place of
the AMP and provides line level outputs for each output channel.
VX link
Control Panel
VX-3000CT
The CT has 9 function keys
and 8 volume control knobs,
and is responsible for providing the system with a hardware user interface.
VX was originally designed with the idea that a fixed volume could be set in advance using software. CT was added to allow the system operator to adjust the volume of Frame's input and output. It also has keys to activate various functions.
2 CTs can be installed per frame in 1 system. This means that up to 80 devices/system can be connected.
Connected with VX link.
VX link
The other one is responsible for sending and receiving audio between different networks.
Since the VX-3000 was originally a system that performed multicast communication, it could only be applied to the same network configuration. For users who want to segment their networks, PM is responsible for unicast communication between different networks.
VX link
(NW 0)
VX link
(NW 1)
VX link
(NW 2)
Detail

## Slide 15
VX-3000 series
Overview
Detail
VX-3000 series can be received audio stream from IP-3000 series
and transmitted it to NX-300 series. Also, can be controlled by the external control device using VX-3000’s remote protocol. In addition it can be controlled by the Modbus protocol.
Basic
configuration
IP-3000 series
NX-300 series
VX-3000 series becomes
terminal AMP of IP-3000 system.
NX-300 series becomes
Zone monitor interface* of VX-3000 system.
Control device can control
VX-3000 series with Original Protocol
Control device can control
VX-3000 series with Modbus Protocol
v.2
v.2
v.2
Detail
v.3
* The NX-300 can only be used as a Zone monitor;
it cannot be used as a separate broadcast output.

## Slide 16
Functions
Broadcast
There are 4 type of broadcast
General broadcast: Live announcement for everyday use and Pre Recorded announcement for shed when necessary
Base pattern broadcast: Continuously broadcasted music
Emergency broadcast: Broadcasting with the highest priority when evacuation is necessary such as in case of fire
Emergency Warning broadcast Emergency broadcasting received from external equipment. Any priority can be set.
v.2
Priority
1024 levels of priority can be set for remote microphone (RM), audio input, built-in sound source (EV), etc. “Priority” determines which input is given priority when broadcasting to the same output.

## Slide 17
Functions
Broadcast
Detail of Broadcast
Details of the broadcast structure are described.
General broadcast: Live announcement for everyday use and Pre Recorded announcement for shed when necessary
Base pattern broadcast: Continuously broadcasted music
Emergency broadcast: Broadcasting with the highest priority when evacuation is necessary such as in case of fire
Emergency Warning broadcast Emergency broadcasting received from external equipment. Any priority can be set.
[D] 4 type of broadcast
[A] 2 Starting Methods
Trigger -> Audio Input + Audio Output + Control Output The audio input and audio output are linked directly to the trigger.
Trigger -> Broadcast Pattern: [Audio Input + Audio Output + Control Output] Once a broadcast pattern is created, this is linked to the trigger.
[B] 7 Types & 1,024 Priorities of Audio Input
[C] 3 Broadcast Patterns
General broadcast Pattern used for General broadcast
Base pattern used for Base pattern broadcast
Emergency broadcast Pattern: used for Emergency broadcast pattern

## Slide 18
Functions
Broadcast
[A] Starting method
There are two starting methods as follows.
Audio Input + Audio Output + Control Output
Activate Broadcast Pattern with audio input, broadcast destination etc. set from trigger such as Key and Control input.
This method is not used for Emergency Warning Broadcast.
Specify the broadcast destination directly from trigger such as Key and Control input.
All 4 broadcast types (General, Base pattern, Emergency, Emergency Warning) can use this method.
Broadcast Pattern:
[Audio Input + Audio Output + Control Output
Detail of Broadcast
Internal Timer
VOX
Internal Timer

## Slide 19
Functions
Broadcast
[A] Starting method
Detail of Broadcast
VOX
A VOX function is a function to automatically output the audio input signals to the set zone by detecting audio input signal level. The VOX function is useful for broadcasting an audio source which doesn't have control output.
Broadcast and Control signal output is started when the VOX gate is open, and stopped when closed. The VOX gate opens when the audio input signal level exceeds the sum level of the threshold level and the hysteresis setting value. Once open, the VOX gate closes after the time set in Hold time elapses when the audio input signal level decreases below the level obtained by subtracting the hysteresis setting value from the threshold level.
Internal Timer
Day Program：Register events for a day (event schedule)
Up to 50 events for a day
Up to 10 days possible to program
Weekly Program：Register Day program for a week
Possible to set Day program for each days of week
Holyday Program：Set public holidays and register the Day Program
Possible to specify the starting date and the ending date
Possible to set Day Program holiday by holiday
Up to 50 days possible to program
In triggers, there are 1) control input and 2) RM key operation, 3) internal timer, and 4) voice activation (VOX). Details of 1) 2) will be introduced in the "System Detail" section. On this page, only the outline of 3) and 4) is introduced.
Broadcast and control output can be started/stopped by the internal timer of the system. Details of the events that can be set for the timer are introduced in the "System Detail" section.
Detail of 1)3)
Detail of 2)

## Slide 20
Functions
Broadcast
Alert
Evacuation
Restoration
Emergency
Emergency Warning
General
BGM
The input (Mic, Internal EV and Audio input) is set above 8 kinds of Input Type and the Priority. The chart on the left shows which input type can be set for which input device (RM, Audio in, built-in EV etc).

## Slide 21
Functions
Broadcast

## Slide 22
Functions
Broadcast
Internal EV is the WAV file written to the Frame with PC software.
These are used for General, BGM, Emergency broadcast
and Pre/Post Chime
File Requirements
PCM, 16bit/48kHz, Mono
Max 1,024 files,
broadcasting simultaneously /1system
Total 400 MB, aprx.72 min.
4 output simultaneously /1frame
v.2
Internal
EV
Detail

## Slide 23
Functions
Broadcast
In v.5 and later, Emergency Warning Broadcast allows the system to change to emergency mode. At this time, Emergency Warning Broadcast is equivalent to Emergency Broadcast.
The advantage of this additional feature is that the system can perform an emergency broadcast using the audio input.
v.5
Emergency
Warning
Audio
Input
Priority 001 - 1024
Emergency Warning broadcast

## Slide 24
Functions
Trigger of activation
Audio input
Audio output (Zone)
Control
output
AUDIO IN 4ch
VX link in 8ch from other frame and PM
EV
Matrix
to AMP & Zones
VX-3004F: max 4 zones
VX-3008F: max 8 zones
VX-3016F: max 16 zones:
Remote
Microphone
(RM)’s AUX
Key
on RM and CT's
Control input
on frame and PM
VX link out 8ch to other frame
Control output
on frame and PM
Inside
WAV file
Internal Timer
Consist of the Broadcast Pattern
Except broadcast using MIC of RM-300X/RM-200SF, ｔhe broadcasts are based on “broadcast pattern” pattern which is comprised of a combination of “Audio input”, “Audio output” and “Control output”, and these patterns are started by the “trigger”.
Broadcast
Input type & Priority
v.5
[C] 3 Broadcast Patterns
Detail of Broadcast

## Slide 25
Functions
General Broadcast Pattern
Broadcast
[C] 3 Broadcast Patterns
Detail of Broadcast
Trigger
- RM key
- Frame’s control input
- Internal timer
- PM’s control input
- CT’s key
Broadcast Pattern
Zone
Patterns
Zone
CO
Patterns
CO
CO
Zone
Single Audio input
・RM’s AUX input
・Frame’s audio input
・Frame’s inside EV
・PM’s audio input
Base Pattern
Trigger
- RM key
- Frame’s control input
- Internal timer
- PM’s control input
- CT’s key
Broadcast Pattern
Zone
Patterns
Zone
Single Audio input
・RM’s AUX input
・Frame’s audio input
・Frame’s inside EV
・PM’s audio input
CO
Patterns
CO
CO
Zone
BGM
Type
“General broadcast pattern” include Audio input – Zones and Control output is activated by the trigger.
Up to 1,024 patterns can be set.
“Base pattern” include Audio input – Zones and Control output is activated by the trigger.
Up to 1,024 patterns can be set.
“Emergency broadcast pattern” is consists of
not only audio input/output but also the “Emergency sequence” .
Emergency sequence
EV1
EV2
EV2
Emergency sequence
EV1
EV2
Emergency sequence
EV1
EV3
EV2
Emergency sequence
EV1
EV2
EV3
30 phase* can be set in 1 “emergency sequence”. *from v.5, v.4 or less: 3 phases
The EV file and phase duration time are set in the phase. Up to 32 “sequence” can be set.
Emergency Broadcast Pattern
Zone
Pattern
Zone
Zone
CO
Pattern
CO
CO
Emergency sequence
EV1
EV2
EV3
Zone
Zone
CO
CO
Zone
Zone
CO
CO
“Emergency broadcast pattern” include 1 sequence. Each phase are set “Zone pattern” and “Control output pattern”.
Up to 1,024 pattern.
Trigger
・RM key
・Frame’s control input
Emergency Broadcast Pattern
Emergency sequence

## Slide 26
Functions
Broadcast
[D] 4 type of broadcast
Detail of Broadcast

## Slide 27
Functions
Broadcast
You can add a zone and a zone pattern with the RM’s key of microphone during general broadcast progress.
You can activate inside or external EV with “one shot” key operation.
You can set zone pattern to talk key directory, can make one-touch talk button.
A small improvement
+
[D] 4 type of broadcast
Detail of Broadcast

## Slide 28
Functions
Broadcast
[D] 4 type of broadcast
Detail of Broadcast

## Slide 29
Functions
Broadcast
“Emergency mode”
When the emergency broadcast is activated, the system turn to the emergency mode. The outline of emergency mode is as follows.
The RM and Frame emergency indicators light red.
The emergency/general hybrid RM’s function is changed to emergency functions; RM chime sound, priority and volume can be changed for emergency-use etc.
General broadcasts and BGM broadcasts are possible in zones where emergency broadcasts are not be broadcasting.
[D] 4 type of broadcast
Detail of Broadcast

## Slide 30
[D] 4 type of broadcast
Detail of Broadcast
Functions
Broadcast
Improvement
2 of Emergency patterns can be activated by 1 trigger.
Emergency Broadcast Pattern 1
Zone
Pattern
Zone
Zone
CO
Pattern
CO
CO
Emergency sequence
EV1
EV2
EV3
Zone
Zone
CO
CO
Zone
Zone
CO
CO
Emergency Broadcast Pattern 2
Zone
Pattern
Zone
CO
Pattern
CO
CO
Emergency sequence
EV4
EV4
EV3
Zone
Zone
Zone
CO
CO
Pat1
Pat2
v.2
A small improvement
1) The priority of RM-300X type can be fixed to emergency level.
2) RM can broadcast
a chime at the time of
general or emergency
broadcast
starting/ending.
3) “Emg. Silence”
EV broadcast can be temporarily muted by RM key or CI in order for the firefighter to find a person who delayed in fleeing.
4) “Emg. Ack.”
The buzzer that sounds at emergency can be stopped with RM key..
5) “Emg. EV broadcast”
The operators can broadcast arbitrary emergency sound sources to arbitrary areas at arbitrary timing using RM keys.
6) One touch key
You can set zone pattern to RM-300X’s talk key directory, can make one-touch talk button.
And can set different content
from the general broadcast.
v.3
+
v.5

## Slide 31
Broadcast
Functions
In v.5 and later, Emergency Warning Broadcast allows the system to change to emergency mode. At this time, Emergency Warning Broadcast is equivalent to Emergency Broadcast.
The advantage of this additional feature is that the system can perform an emergency broadcast using the audio input.
v.5
[D] 4 type of broadcast
Detail of Broadcast

## Slide 32
Functions
FBS
Audio
Processing
In this movie, other equipment is used. VX-3000’s FBS function can set FBS filter automatically.
Demonstration of the FBS
Feedback Suppressor (FBS) can be set on RM input or AUDIO IN.
Feedback occurs when an acoustic loop is made among the MIC, AMP and SP. When the MIC and SP are placed in the same space, the sound from the SP can also be received by the MIC, AMP further, and passed out through the SP again, and part of this amplified sound may again be revived by MIC. Such repeating phenomenon creates the feedback.
AUDIO IN 4ch
VX link in 8ch from other frame
EV
Matrix
to AMP & Zones
VX-3004F: max 4 zones
VX-3008F: max 8 zones
VX-3016F: max 16 zones
Remote
Microphone
(RM)’s AUX
VX link out 8ch to other frame
Inside
WAV file
DSP
FBS
DSP
Volume degreasing, Comp., Filter, VOX *, Delay** function are set each input/output channels.
* input only
** output only
DSP
v.2
v.2

## Slide 33
This page is used for “replay” of next page.
Do not erase this page.

## Slide 34
Functions
ANC
AUDIO IN 4ch
VX link in 8ch from other frame
EV
Remote
Microphone
(RM)’s AUX
VX link out 8ch to other frame
Inside
WAV file
Ambient Noise Control (ANC) function adjusts BGM/announcement
sound volume to match changes in listening area noise levels.
AUDIO IN can be changed sensing MIC input.
(VX-3008F/16F: only 1 ch.)
Output
Ambient Noise
Rush
Hour
Rush Hour
DSP
FBS
DSP
Click
Click
Replay
v.2
to AMP & Zones
VX-3004F: max 4 zones
VX-3008F: max 8 zones
VX-3016F: max 16 zones
ANC
Audio
Processing

## Slide 35
Functions
Monitoring
Zone Audio Monitor
Audio signal during broadcast can be monitored by the remote mic or NX-300.
The SP line where is connected other frame can be monitored.
The SP line separated by SS can be monitored.
AMP
AMP
matrix
AMP
AMP
AMP
matrix
VX link (Network)
AMP
SS
Monitor Speaker
Monitor: Flame0 - Zone1
Monitor: Flame0 - Zone2
Monitor: Flame0 - Zone3
Monitor: Flame0 - Zone4
Monitor: Flame1 - Zone1
Monitor: Flame1 - Zone2
The broadcast can be monitored by NX-300.
The number of output channel is 16 channels, 8 units. Several NX-300’s channels can be output broadcast signal of 1 zone.
v.2

## Slide 36
Functions
Integration
with
Ext.system
Remote Protocol and IP-3000 connection
VX-3000 system can be controlled with its remote protocol.
IP-3000 series
VX-3000 series becomes
terminal AMP of IP-3000 system.
VX-3000 series
Max 32 Audio Streams
Remote Protocol: Multicast address, Zone etc.
Multicast
address
Remote Protocol: Audio In , Zone etc.
Remote Protocol: Audio file playback etc.
Digital Announcer
Control server
VX-3000 system can receive the audio streaming from IP-3000 system.
VX link (Network)
VX link (Network)
VX-3000 series
IP-3000’s system manager is needed to be customized for sending this control command to VX-3000 system.
v.2
VX-3000 system can receive up to 32 stream from external system

## Slide 37
Functions
Modbus Protocol connection
The VX-3000 System responds to the request from an external device using the Modbus protocol and returns the broadcast status, control terminal status, fault status and so on.
Modbus Protocol:
Modbus server
VX link (Network)
VX-3000 series
What is Modbus® protocol? http://www.modbus.org/faq.php
Modbus Protocol is a messaging structure developed by Modicon in 1979. It is used to establish master-slave/client-server communication between intelligent devices. It is a de facto standard, truly open and the most widely used network protocol in the industrial manufacturing environment. It has been implemented by hundreds of vendors on thousands of different devices to transfer discrete/analog I/O and register data between control devices. It's a lingua franca or common denominator between different manufacturers. One report called it the "de facto standard in multi-vendor integration". Industry analysts have reported over 7 million Modbus nodes in North America and Europe alone.
Integration
with
Ext.system
v.3

## Slide 38
Functions
Web Browser Controller
It is also possible to custom-make a control system using a web browser.
This is an example system that is being produced in the AP region.
Web Browser
Audio
Server
VX link (Network)
VX-3000 series
Integration
with
Ext.system
Remote Protocol: Audio In , Zone etc.
Audio signal (analog)

## Slide 39
Indicators (always)
Fault Log
Buzzer from frame
Functions
Detection Items
Analog Link
VX link A and B
DC power
DS-LINK
AMP
RM
Control input
External equipment via control input
Speaker line Open/Short/Ground fault
Failure detection & Indication
The system is equipped with error detect and indication functions.
Indication
Patterns are assigned to various indicators.
100 Fault Log (in 10,000 event log)
Control Output
RM’s key indicator
Remote Protocol
E-mail
Buzzer from each frame
Assignable Fault LEDs These LEDs are initially assigned fault indications of the items listed in the silk, but these LEDs can also be assigned the Failure Output patterns.
Initial setting is just what written by the silk on front panel.
You can make
“Failure output pattern”
using these menu.
Surveillance
Individually
v.2
Failure Output Pattern
Multiple detection items can be patterned to up to 32 patterns in setting software. For example, it may be assembled at the installation position of Frame, or it may be assembled only by breakdown of AMP.
The setting software screen
Failure Output Pattern
Detection Items
Analog Link, VX link,
DC power, DS-LINK,
AMP, RM, Control input, External equipment,
Speaker line
Indicators (assignable)
Control Output
RM’s key indicator
E-mail
Indicators ( set as “event”)
RM’s key indicator
LED on frame
v.2
v.3
The key next to the indicator has an acknowledge function.

## Slide 40
Functions
Impedance method
Standard method without EOL unit
The system compares initial impedance and observing impedance
Able to check the value of initial impedance and adjust the value with setting software
EOL method
The method using the EOL unit and shielded SP line
The system use the specified value of EOL unit to judge
Speaker line detection
The system is equipped with error detect and indication functions.
• Applies to various types of speaker cables (no need to use shielded type cables).
• Needs no additional detector to be connected to the speaker line.
• Provides less precision in detection of speaker cable disconnection than the EOL method.
• Detects speaker cable disconnection precisely.
• Needs shielded speaker cables to be used.
• Needs an EOL unit to be connected to the speaker line.
VX-3004F
EOL
SX-200EL
VX-3008F
or
VX-3016F
EOL
VM-300SV
Control input
The system separates SP line detected failure without stopping broadcast of other Zone after having detected the failure of SP line.
Surveillance

## Slide 41
Functions
A standby amplifier can be reserved for up to 31 regular AMP.
AMP
AMP
AMP
AMP
X
matrix
AMP
AMP
AMP
X
sb AMP
matrix
AMP
AMP
AMP
sb AMP
matrix
AMP
VX link (Network)
VX link (Network)
Frame 01
Frame 00
Frame 02
B A
B A
B A
X
VX link (Network)
The frame has 2 ports of Network. The dualization of the communication line is realized by connecting VX link in ring form with two ports comprised to each frame.
AMP
Battery
AMP
AMP
AMP
Max 25A, 8ch
Max 2,000W
Max 5A, 3ch
AC 220-230V
50/60W
DS link
Power supply backup is included in DS.
AC power and
Battery : When a problem occurs in AC,
the system is able to continue
broadcast using Battery.
Power supply
Redundant
Detail
Detail
Detail
Possible broadcasting is selective from the following.
- Emergency/Emg.Warning only
- Emergency/Emg.Warning & General only
- Emergency/Emg.Warning, General & BGM

## Slide 42
Functions
CPU Off Mode and Analog Link
Redundant
Detail
Detail
Detail
The CPU off function permits the all-zone calls to be made from the RM-200SF or RM-300X by bypassing the CPU normally used by the VX-3000F and using an analog link instead. This function is usually used if a system failure is preventing normal broadcasts from being made.
Analog Link (Max: 800m)
Frame
Frame
Frame
OUT IN
OUT IN
OUT IN
By pressing the key under the red cover of the RM-300X for 4 seconds, the system will shift to CPU OFF mode.
By turning off the CPU Switch of the RM-200SF, the system is shifted to the CPU OFF mode.
Broadcasts of RMs with the same priority are mixed.

## Slide 43
Functions
Redundant
System Manager
Detail
Detail
Detail

## Slide 44
Functions
Redundant
System Manager
Detail
Detail
Detail
The running of the divided systems
From ver.2, even if the VX link is disconnected, each localized system can be keep to run.
In the left figure case, ID:0 is failure and the VX link is disconnected. Each localized system 1 and 2 can be keep to run. But it can not communicate 1 and 2 each other.
v.2
VX link
(Network)
VX link
(Network)
ID:0 frame
System manager
Localized System 1
Localized System 2
Localized System 1
X
X

## Slide 45
Functions
VX-3000 is equipped with useful functions for maintenance using the Hard and the Software.
Log : receiving from VX-3000 system, Open from file and Saving to file.
The log is distinguished from “General” and “Error”.
“General”: Max 10,000, “Error”: Max 100
Unit status :
allowing the following information to be confirmed in real time:
- Individual unit's setting and connection status
- Individual unit's operation mode and failure status
- Individual unit's version information
- Failure status of amplifiers, speaker lines and power supply
Broadcasting status :
broadcast pattern being activated and audio signal
input/output status can be confirmed online.
Terminal status :
control input and output statuses can be confirmed
in real time.
Maintenance software: Log screen
Maintenance software: Broadcast status screen
Maintenance
• OS: Windows 7 (32 bit/64 bit), Windows 8.1 (32 bit/64 bit), Windows 10 (32 bit/64 bit)
• Required Component: Microsoft .NET Framework 4.5.2 (when the OS is Windows 7 or Windows 8.1)
• CPU: 1 GHz or faster • Memory: 1 GB or more

## Slide 46
Functions
VX-3000 is equipped with useful functions for maintenance using the Hard and the Software.
Surveillance Mail
The system can be notified by e-mail at the time of failure and failure reset via SMTP server.
You can create 40 mailing lists, not just one address.
Maintenance
Disablement of Emergency Activation
Emergency broadcasting activation with CI from the fire alarm device can be temporarily invalidated by RM key operation. This is a function for not activating emergency broadcast by mistake during maintenance.
There is Re-sending function.
v.3
v.3

## Slide 47
Functions
VX-3000 is equipped with useful functions for maintenance using the Hard and the Software.
Access Permission
Functions that can be set in the PC setting software can be restricted for each user.
The following 4 levels can be set.
Possible to set each password.
(End User don’t require password.)
Maintenance
v.5
End User
Refer unit status and log.
Advanced End User
Possible to configure EV setting for General/BGM, and timer schedule.
Installer
Possible to configure everything except updating firmware and changing password
Administrator
No limitation
4 LEVELS . |  | End User | Advanced End User | Installer | Admin.
File (F) | New | - | - | @ | @
 | Open | - | @ | @ | @
 | Save | - | @ | @ | @
 | Save as | - | - | @ | @
 | Data output（Setting data） | - | - | @ | @
 | Data output（RM Label) | - | - | @ | @
 | Exit | - | @ | @ | @
Communication (C) | Setting＆EV upload | - | @ | @ | @
 | Setting＆EV download | - | @ | @ | @
 | Timer setting | - | @ | @ | @
Maintenance(M) | Maintenance | (@) | (@) | @ | @
 | Unit detection, network setting | - | - | @ | @
Help(H) | Access permission | - | - | - | @
 | Version | - | @ | @ | @

## Slide 48
Functions
Using “TOA finder”: PC software , the each of frames can be scanned.
IP address, SM are set to the frames by this software.
Network setting
In fact, you can give the IP address to the frames automatically
without using the software.
The frames be assigned different ID Numbers.
In automatically mode,
network values are determined like the following.
IP address : 192.168.14.xx
("xx" is one larger than ID Number.)
Subnet mask : 255.255.255.0
Default gateway : 0.0.0.0
Setting
• OS: Windows 7 (32 bit/64 bit), Windows 8.1 (32 bit/64 bit), Windows 10 (32 bit/64 bit)
• Required Component: Microsoft .NET Framework 4.5.2 (when the OS is Windows 7 or Windows 8.1)
• CPU: 1 GHz or faster • Memory: 1 GB or more

## Slide 49
Functions
Functions, System configuration and broadcast pattern are set by PC software,
Basic / System configuration / Broadcast setting
Setting
• OS: Windows 7 (32 bit/64 bit), Windows 8.1 (32 bit/64 bit), Windows 10 (32 bit/64 bit)
• Required Component: Microsoft .NET Framework 4.5.2 (when the OS is Windows 7 or Windows 8.1)
• CPU: 1 GHz or faster • Memory: 1 GB or more

## Slide 50
Functions
Functions, System configuration and broadcast pattern are set by PC software,
Basic / System configuration / Broadcast setting
Setting
• OS: Windows 7 (32 bit/64 bit), Windows 8.1 (32 bit/64 bit), Windows 10 (32 bit/64 bit)
• Required Component: Microsoft .NET Framework 4.5.2 (when the OS is Windows 7 or Windows 8.1)
• CPU: 1 GHz or faster • Memory: 1 GB or more
Setting information can be exported as a dedicated .vxd file
or .csv file.
Mic labels can be printed using setting data.
v.3

## Slide 51
System detail
VX-3004F
AMP
AMP
AMP
AMP/sb AMP
matrix
VX-3008F
AMP
AMP
sb AMP
SS
matrix
VX-3016F
AMP
AMP/sb AMP
SS
matrix
Like the VX-2000
similar to VM-3000
The frame is a device as a master constituting a system.
There are three kinds of the frames. Each module has audio input and output. There is no system manager like the SX-2000 system.
Module-type AMP is incorporated in the frame.
LO
v.5.1
Since ver.5.10, it is now possible to install LO (Line Output module) instead of AMP.
Frame
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference

## Slide 52
System detail
VX-3004F
AMP
AMP
AMP
AMP/sb AMP
matrix
VX-3008F
AMP
AMP
sb AMP
SS
matrix
VX-3016F
AMP
AMP/sb AMP
SS
matrix
Like the VX-2000
similar to VM-3000
The frame is a device as a master constituting a system.
There are three kinds of the frames. Each module has audio input and output. There is no system manager like the SX-2000 system.
Module-type AMP is incorporated in the frame.
AMP
AMP
AMP
AMP
SP out
input
ATT
control
control
Exp
DC
AMP
AMP
AMP
SP out
input
ATT
control
control
Exp
DC
AMP
AMP
SP out
input
ATT
control
control
Exp
DC
SP out
LO
v.5.1
Since ver.5.10, it is now possible to install LO (Line Output module) instead of AMP.
Frame
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference

## Slide 53
System detail
Basically, these cross points of the output matrix are chosen automatically.
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference

## Slide 54
System detail
Control | 16ch | Non-voltage Assignable some functions
FDS | 2ch | +24V/-24V switchable Assignable functions
Input
General control | 8ch | No voltage, Open collector Assignable functions
Fault/CPU off Control | 3ch | No voltage, Open collector General fault: 1ch CPU fault: 1ch CPU off: 1ch
ATT control | Ref* | Non voltage, Relay, Assignable functions * VX-3004F/3008F: 8ch * VX-3016F: 16ch
Output
AUDIO IN
N 1
MIX
When N > 1 (; N=2, 3, or 4)
N can connect to N oneself or 1.
AUDIO IN
N M 1
When N > M > 1 (; N, M =2,3,or4)
If M connect to M oneself
N can choose N oneself , M, or 1.
MIX
You can mix the several audio input signal to 1 channel with setting software.
This MIX function has the following limitation.
A small improvement
It is difficult to explain this limitation by general words. . .
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference

## Slide 55
System detail
Control | 16ch | Non-voltage Assignable some functions
FDS | 2ch | +24V/-24V switchable Assignable functions
Input
General control | 8ch | No voltage, Open collector Assignable functions
Fault/CPU off Control | 3ch | No voltage, Open collector General fault: 1ch CPU fault: 1ch CPU off: 1ch
ATT control | Ref* | Non voltage, Relay, Assignable functions * VX-3004F/3008F: 8ch * VX-3016F: 16ch
Output
MIX
When N > 1 (; N=2, 3, or 4)
N can connect to N oneself or 1.
When N > M > 1 (; N, M =2,3,or4)
If M connect to M oneself
N can choose N oneself , M, or 1.
MIX
You can mix the several audio input signal to 1 channel with setting software.
This MIX function has the following limitation.
A small improvement
It is difficult to explain this limitation by general words. . .
When AUDIO IN1,2,3 are not mixed,
AUDIO IN4 can choose AUDIO IN1 to 4.
When AUDIO IN1,2,3 are mixed to AUDIO IN1,
AUDIO IN4 can choose only AUDIO IN1 and 4.
AUDIO IN MIX screen on Setting software
AUDIO IN
N M 1
AUDIO IN
N 1
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference

## Slide 56
System detail
Internal EV is the WAV file written to the Frame with PC software.
These are used for General, BGM, Emergency broadcast
and Pre/Post Chime
File Requirements
PCM, 16bit/48kHz, Mono
Max 1,024 files,
broadcasting simultaneously /1system
Total 400 MB, aprx.72 min.
4 output simultaneously /1frame
v.2
Internal
EV
:
File 0001
File 0002
File 0003
File 0004
:
File 1024
Multiple frames hold the same files.
File 0001
File 0002
Silence
EV message
0001
EV message
0002
EV message
1024
File 1024
File 0004
File 0004
File 0003
...
Files are handled in list (EV message No.) consisting of up to 8 files.
Silence time and number of repetitions are also set in this list.
Up to 1024 lists will be created.
:
:
EV message
0001
EV message
0002
EV message
1024
0001
0002
1024
Different EV messages (file list) can be broadcast simultaneously in multiple frames.
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference

## Slide 57
System detail
DSP | Input | Output
Volume | 0 to -70 dB | 0 to -70 dB
Filter | 3 point Type: PEQ, HPF(6dB), HPF(12dB), LPF(6dB), HPF(12dB), Low Shelving, High Shelving Frequency, Gain, Q | 6 point Type: PEQ, HPF(6dB), HPF(12dB), LPF(6dB), HPF(12dB), Low Shelving, High Shelving All pass, Notch, Horn EQ Frequency, Gain, Q
VOX | (Only AUDIO IN) Threshold, Hysteresis, Hold time, Related C.O. Zone/Zone pattern | -
COMP | Threshold, Ratio, knee type, Attack time, Release time, Gain | -
Delay | - | Delay time
For VX-3008F, 3016F, all Zones are set with only one parameter.
It is not possible to set different settings for each Zone.
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference

## Slide 58
System detail
DSP | Input | Output
Volume | 0 to -70 dB | 0 to -70 dB
Filter | 3 point Type: PEQ, HPF(6dB), HPF(12dB), LPF(6dB), HPF(12dB), Low Shelving, High Shelving Frequency, Gain, Q | 6 point Type: PEQ, HPF(6dB), HPF(12dB), LPF(6dB), HPF(12dB), Low Shelving, High Shelving All pass, Notch, Horn EQ Frequency, Gain, Q
VOX | (Only AUDIO IN) Threshold, Hysteresis, Hold time, Related C.O. Zone/Zone pattern | -
COMP | Threshold, Ratio, knee type, Attack time, Release time, Gain | -
Delay | - | Delay time
For VX-3008F, 3016F, all Zones are set with only one parameter.
It is not possible to set different settings for each Zone.
FBS Feedback Suppresser
Feedback Suppressor (FBS)
can be set on each RM input(RF link) or AUDIO IN.
There are 7 points filters in one FBS.
v.2
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference

## Slide 59
System detail
ANC
ANC is used same method at DP-L2.
The sensor MIC can be connected to AUDIO IN.
The MIC can be set up to the following numbers.
VX-3004F: 4, VX-3008F: 1, VX-3016F: 2
The sensor MIC can be assigned to output channel to control volume. Within the same frame, one sensor microphone can cover multiple ZONE.
ANC
Input
Output
ANC Ambient Noise Control
v.2
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference

## Slide 60
System detail
v.2
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference
ANC
ANC is used same method at DP-L2.
The sensor MIC can be connected to AUDIO IN.
The MIC can be set up to the following numbers.
VX-3004F: 4, VX-3008F: 1, VX-3016F: 2
The sensor MIC can be assigned to output channel to control volume. Within the same frame, one sensor microphone can cover multiple ZONE.
ANC
Input
Output
ANC Ambient Noise Control
(4) Reference noise level
(3) Sensor level; measured by Sensor mic
(B) Output level with ANC function
(A) Output level without ANC function: 0dB
(1) Max level *negative value based on (A)
(2) Min level *negative value based on (A)
(5)Ratio :
(4’) Adjust Zero
time
signal level
(dBV)
signal level
(dB)
ANC Parameters & Setting <detail>
Parameters
ANC operates with parameters (1)-(5).
(1) Maximum output level when ANC is enabled
(2) Minimum output level when ANC is enabled; This is the output level when the site is quiet.
(3) Average noise level measured by sensor microphone
(4) When (3) exceeds this level, automatic volume adjustment starts.
(5) Ratio of output increase to noise increase
Also,
(A) Output level when ANC is disabled
(B) Output level after automatic volume adjustment by ANC
Setting Procedure
Basically, ANC can only be configured properly when the site is quiet.
1: Decide (1): Usually 0dB is acceptable.
Output the loudly noise from the portable SP and check that (1) is sufficient.
Preview broadcast of max level can be done with key (1’).
2: Decide (2): This should be sound enough to hear when the site is the quietest.
Preview broadcast of min level can be done with key (2’).
3: Measure (4) when the site is the quietest
4: Check if there is a big difference between (3) & (4) when the site is the quietest.
If not, use (4’) to adjust.
5: Decide (5); Usually “3:3” is sufficient.
6: Use Portable SP to output the maximum volume noise and check the automatic volume change of the output.
Software Screen
ANC parameters are placed 3 screens of setting software.
(1)
(2)
(5)
(4’)
Main screen
Sound settings - ANC
(1’)
(2’)
Maintenance screen
ANC Setting
ANC Reference
(3)
(4)
Portable SP
For the demonstration, make great settings to make it easier
for audience to understand the effect.
(1) is large, (2) is small, (3 ') is short, (5) is large,
In realistic installations, it will be annoying if the volume changes frequently.
A mild setting is preferred.
(1) is large, (2) Be careful not to be too small, (3 ') is long, (5) is Basically “3:3”
ANC
(3) is calculated from the recordings
during the sampling time (3’).
The shorter (3’) is, the more sensitive (3) will follow the actual noise change.
Even if the Sensor level (3) is too high,
the Output level (B) will not be higher than this level.
(3’)

## Slide 61
Frame
Common topics: Control
System detail
Main function is ATT bypass control when the system progress emergency broadcast. But you can set other function to the “ATT control” output.
Control | 16ch | Non-voltage Assignable some functions
Emergency Control | 2ch | +24V/-24V switchable Assignable functions
Input
Control General | 8ch | No voltage, Open collector Assignable functions
Control Fault/CPU off | 3ch | No voltage, Open collector General fault: 1ch CPU fault: 1ch CPU off: 1ch
ATT/Control | Ref* | Non voltage, Relay, Assignable functions * VX-3004F/3008F: 8ch * VX-3016F: 16ch
Output
Some fire alarm machine is equipped with FDS output which +24V/-24V switching. This connecter is for connecting the output of the fire alarm machine.
VX
Fire
alarm
FDS input
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference

## Slide 62
System detail
Input
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference

## Slide 63
 |  | Frame |  | RM's key |  | RM-500 | RM-500 | PM | CT
 |  | CI | Timer | Emg Emg/Gen | Gen | CI | Key | CI | Key
General Bro. Pattern | Activate (level) | @ | @ | @* | @* | @ | @* | @ | 
 | Activate (pulse) | @ |  | @* | @* | @ | @* | @ | @
Base pattern | Activate | @ | @ | @ | @ |  | @ | @ | @
 | Interrupt | @ | @ | @ | @ |  | @ | @ | @
Volume Adjustment | Zone volume (level) | @ | @ |  |  |  |  | @ | 
 | Zone volume (pulse) | @ | @ | @ | @ |  | @ | @ | @
 | Input volume (level) | @ |  |  |  |  |  | @ | 
 | Input volume (pulse) | @ |  | @ | @ |  | @ | @ | @
Time adjustment |  | @ |  |  |  |  |  | @ | 
Emergency Bro. Pattern | Start | @ |  | @ |  |  |  |  | 
 | Stop | @ |  | @ |  |  |  |  | 
 | Start and Stop | @ |  | @ |  |  |  |  | 
Emergency Sequence | Stop | @ |  | @ |  |  |  |  | 
 | Phase shift | @ |  | @ |  |  |  |  | 
Emergency Mode | Reset | @ |  | @ |  |  |  |  | 
 | Silence | @ |  | @ |  |  |  |  | 
 | EV Broadcast |  |  | @ |  |  |  |  | 
 | Acknowledge |  |  | @ |  |  |  |  | 
Emergency Warning Broadcast |  | @ |  | @ | @ | @ | @ | @ | @
EV(General/BGM) Playback |  |  |  | @ | @ |  | @ |  | @
Malfunction | Fault Acknowledge | @ |  | @ | @ |  |  |  | 
 | Fault Reset | @ |  | @ | @ |  |  |  | 
 | External Fault Input | @ |  | @ | @ |  |  |  | 
Pre Select | Pattern |  |  | @ | @ |  | @ |  | @
 | Indovidual |  |  | @ | @ |  | @ |  | @
 | Clear |  |  | @ | @ |  | @ |  | @
Intended Control in/out | Input Operation |  |  | @ | @ |  | @ |  | @
 | Output Operation (level/pulse) |  | @ | @ | @ |  | @ |  | @
Maintenance | RM Broadcast Status |  |  | @ | @ |  | @ |  | 
 | Audio Monitor |  |  | @ | @ |  |  |  | 
 | Disablement of EMG control from CI |  |  | @ |  |  |  |  | 
 | Lamp Test |  |  | @ | @ |  |  |  | 
Power ON |  | @ | @ | @ | @ | @ | @ | @ | @
Talk |  |  |  |  | @ |  | @ |  | 
Emergency Talk |  |  |  | @ |  |  |  |  | 
General Talk |  |  |  | @ |  |  |  |  | 
System detail
Control | 16ch | Non-voltage Assignable some functions
Emergency Control | 2ch | +24V/-24V switchable Assignable functions
Input
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference
NO/NC
NO/NC
NO/NC
NO/NC
NO/NC
NO/NC
NO/NC
NO/NC
These are possible configurable features. indicates that switching between normally open and normally closed is possible.
NO/NC
Functions
which is activated by Frame’s CI

## Slide 64
Frame
Common topics: Internal Timer
System detail
Each frame has an internal timer, which can activate several functions.
Day Program：Register events for a day (event schedule)
Up to 50 events for a day
Up to 10 days possible to program
Weekly Program：Register Day program for a week
Possible to set Day program for each days of week
Holyday Program：Set public holidays and register the Day Program
Possible to specify the starting date and the ending date
Possible to set Day Program holiday by holiday
Up to 50 days possible to program
Type of Program
Functions
which is activated by program
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference
 |  | Frame |  | RM's key |  | RM-500 | RM-500 | PM | CT
 |  | CI | Timer | Emg Emg/Gen | Gen | CI | Key | CI | Key
General Bro. Pattern | Activate (level) | @ | @ | @* | @* | @ | @* | @ | 
 | Activate (pulse) | @ |  | @* | @* | @ | @* | @ | @
Base pattern | Activate | @ | @ | @ | @ |  | @ | @ | @
 | Interrupt | @ | @ | @ | @ |  | @ | @ | @
Volume Adjustment | Zone volume (level) | @ | @ |  |  |  |  | @ | 
 | Zone volume (pulse) | @ | @ | @ | @ |  | @ | @ | @
 | Input volume (level) | @ |  |  |  |  |  | @ | 
 | Input volume (pulse) | @ |  | @ | @ |  | @ | @ | @
Time adjustment |  | @ |  |  |  |  |  | @ | 
Emergency Bro. Pattern | Start | @ |  | @ |  |  |  |  | 
 | Stop | @ |  | @ |  |  |  |  | 
 | Start and Stop | @ |  | @ |  |  |  |  | 
Emergency Sequence | Stop | @ |  | @ |  |  |  |  | 
 | Phase shift | @ |  | @ |  |  |  |  | 
Emergency Mode | Reset | @ |  | @ |  |  |  |  | 
 | Silence | @ |  | @ |  |  |  |  | 
 | EV Broadcast |  |  | @ |  |  |  |  | 
 | Acknowledge |  |  | @ |  |  |  |  | 
Emergency Warning Broadcast |  | @ |  | @ | @ | @ | @ | @ | @
EV(General/BGM) Playback |  |  |  | @ | @ |  | @ |  | @
Malfunction | Fault Acknowledge | @ |  | @ | @ |  |  |  | 
 | Fault Reset | @ |  | @ | @ |  |  |  | 
 | External Fault Input | @ |  | @ | @ |  |  |  | 
Pre Select | Pattern |  |  | @ | @ |  | @ |  | @
 | Indovidual |  |  | @ | @ |  | @ |  | @
 | Clear |  |  | @ | @ |  | @ |  | @
Intended Control in/out | Input Operation |  |  | @ | @ |  | @ |  | @
 | Output Operation (level/pulse) |  | @ | @ | @ |  | @ |  | @
Maintenance | RM Broadcast Status |  |  | @ | @ |  | @ |  | 
 | Audio Monitor |  |  | @ | @ |  |  |  | 
 | Disablement of EMG control from CI |  |  | @ |  |  |  |  | 
 | Lamp Test |  |  | @ | @ |  |  |  | 
Power ON |  | @ | @ | @ | @ | @ | @ | @ | @
Talk |  |  |  |  | @ |  | @ |  | 
Emergency Talk |  |  |  | @ |  |  |  |  | 
General Talk |  |  |  | @ |  |  |  |  | 
Notes: 表追加

## Slide 65
Frame
System detail
Common topics: others
All mandatory indications by EN54-16
Status indication for each speaker line
Fault acknowledge and lamp test button
Inside EV WAV, PCM, 16bit/48kHz, Mono, Max 1,024 files, Total 80min, 4 output simultaneously
Module AMP unit, easy installation/replacement from front side.
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference
Line Output Module
VX-300LO
v.5.1
Since ver.5.10, it is now possible to install LO (Line Output module) instead of AMP module. Since F.W.ver.5.2, SP line surveillance pilot tone is no longer output from the LO.

## Slide 66
VX-3004F
System detail
AMP
AMP
AMP
AMP
matrix
Max 4 AMP – 4 AB Zone
AMP
AMP
AMP
Max 3 AMP – 3 AB Zone & 1sbAMP
X
sb AMP
matrix
or
AMP
matrix
AMP
matrix
sbAMP
AMP
matrix
AMP
AMP
matrix
AMP
AMP
VX-3004F has multi-route structure. Each zone has exclusive AMP.
Up to 4 different source can be broadcasted to 4 different zones.
Appearance
Other variation
matrix
sbAMP
matrix
NG
(without AMP)
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference
Frame

## Slide 67
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference
AMP
matrix
AMP
matrix
sbAMP
AMP
matrix
AMP
AMP
matrix
AMP
AMP
Other variation
matrix
sbAMP
matrix
NG
(without AMP)
System detail
VX-3004F
AMP
AMP
AMP
AMP
matrix
Max 4 AMP – 4 AB Zone
AMP
AMP
AMP
Max 3 AMP – 3 AB Zone & 1sbAMP
X
sb AMP
matrix
or
VX-3004F has multi-route structure. Each zone has exclusive AMP.
Up to 4 different source can be broadcasted to 4 different zones.
Up to 4 amps
- 1-zone - 1 amp,
4AB-zones
- 3 AB zones
+ standby amp
AMP
AMP
AMP
AMP
matrix
AMP
AMP
AMP
Max 3AMP – 3Zone & 1sbAMP
X
sb AMP
matrix
or
“AB zone” is...
AMP
AMP
AMP
AMP
matrix
Zone 1 - A
Zone 1 - B
The “AB zone” is the wiring method that the Fire Protection Law of German requires.
2 SP lines are installed in 1 zone.
Even if 1 line has problem,
this system can continue broadcasting without interruption.
In EMEA region “AB wiring SP” is soled.
The speakers have 2 unit in 1 cabinet.
BS-250AB-EB
PC-245AB-EB
TOA’s “AB line” method, even if A line has any problem, it does not effect another B line. B line is able to keep broadcasting without interruption.
Appearance
Frame

## Slide 68
System detail
AMP
AMP
sbAMP
matrix
Max 2AMP – 8 Zone & 1sbAMP
SS
Setting A
Setting B
Setting C
AMP
SS
AMP
Covered by
AMP
AMP
AMP
SS
AMP
Covered by
AMP
AMP
Covered by
AMP
SS
AMP
Covered by
AMP
AMP
Covered by
Covered by
AMP
AMP
equipped with 2in/8out speaker selector
You can arrange the zones which these two AMPs cover.
VX-3008F
VX-3008F has 2 bus line and 8 zone speaker selector. Using speaker selector, the system can broadcasts to many zones with only 1 AMP.
Appearance
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference
Frame

## Slide 69
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference
System detail
AMP
AMP
sbAMP
matrix
Max 2AMP – 8 Zone & 1sbAMP
SS
AMP
SS
AMP
Covered by
AMP
AMP
AMP
SS
AMP
Covered by
AMP
AMP
Covered by
AMP
SS
AMP
Covered by
AMP
AMP
Covered by
Covered by
AMP
AMP
equipped with 2in/8out speaker selector
You can arrange the zones which these two AMPs cover.
VX-3008F
VX-3008F has 2 bus line and 8 zone speaker selector. Using speaker selector, the system can broadcasts to many zones with only 1 AMP.
Appearance
Allocation for all zone broadcasting
in CPU off mode is set by DipSW.
Frame

## Slide 70
equipped with 2in/8out speaker selector
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference
Frame
System detail
Setting A
Setting B
Setting C
AMP
AMP
sbAMP
matrix
SS
VX-3008F
AMP
SS
AMP
Covered by
AMP
AMP
AMP
SS
AMP
Covered by
AMP
AMP
Covered by
AMP
SS
AMP
Covered by
AMP
AMP
Covered by
Covered by
AMP
AMP
You can arrange the zones which these two AMPs cover.
Max 2AMP – 8 Zone & 1sbAMP
500W
SS
500W
Covered by
AMP
AMP
500W
SS
500W
Covered by
AMP
AMP
Covered by
500W
SS
500W
Covered by
AMP
AMP
Covered by
Covered by
AMP
AMP
Connected up to 500W
on all 8 SP lines
Connected up to 1,000W
on all 8 SP lines
Used for the Case to use two AMP to the maximum, and to connect SP (less than 1,000W)
Setting like this, You can use AMP efficiently if you know the common zone and the non-common zone clearly.
Same structure at VM-3000.
Used for the case that both 2 sources (like MIC and BGM) to all zone.
Total up to
500 - 1000W
VX-3008F has 2 bus line and 8 zone speaker selector. Using speaker selector, the system can broadcasts to many zones with only 1 AMP.
Appearance

## Slide 71
System detail
AMP
AMP
matrix
Max 2 AMP – 16 Zone
SS
AMP
Max 1 AMP – 16 Zone & 1 standby AMP
X
sb AMP
matrix
SS
VX-3016F
VX-3016F has 2 bus line and 16 zone speaker selector. Using speaker selector, the system can broadcasts to many zones with only 1 AMP.
or
Appearance
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference
Frame

## Slide 72
System detail
AMP
AMP
matrix
Max 2 AMP – 16 Zone
SS
AMP
Max 1 AMP – 16 Zone & 1 standby AMP
X
sb AMP
matrix
SS
VX-3016F
VX-3016F has 2 bus line and 16 zone speaker selector. Using speaker selector, the system can broadcasts to many zones with only 1 AMP.
or
Appearance
3016F does not have this function...
But using DipSW.
You can choose the following 2 modes.
AMP 1 ----- Zone 1 -16
AMP 1 ----- Zone 1 - 8 AMP 2 ----- Zone 9 - 16
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference
Frame

## Slide 73
VX-3008F
VX-3008F
sb AMP
VX-3016F
VX-3016F
matrix
matrix
VX-3008F
VX-3008F
VX-3008F
VX-3008F
AMP
SS
SS
matrix
AMP
sb AMP
SS
SS
matrix
AMP
These two frames can be used as expansion speaker selector. Up to 3 additional frames without AMP can be connected to main frame. But different model can not be connected. Each frames are connected with “Expansion” connecter.
AMP
AMP
SS
SS
SS
SS
AMP
AMP
System detail
VX-3008F/3016F : SS expansion
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference
Frame

## Slide 74
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference
VX-3008F
VX-3008F
sb AMP
VX-3016F
VX-3016F
matrix
matrix
VX-3008F
VX-3008F
VX-3008F
VX-3008F
AMP
SS
SS
matrix
AMP
sb AMP
SS
SS
matrix
AMP
These two frames can be used as expansion speaker selector. Up to 3 additional frames without AMP can be connected to main frame. But different model can not be connected. Each frames are connected with “Expansion” connecter.
AMP
AMP
SS
SS
SS
SS
AMP
AMP
System detail
VX-3008F/3016F : SS expansion
VX-3008F
VX-3008F
sb AMP
matrix
AMP
SS
SS
matrix
AMP
VX-link (Network)
Audio input, RM, Control input and output of the frame as expansion are available. The signal to these input are send the main frame equipped with AMP via VX link (Network).
VX-3016F has only 1ch expansion connecter. Then when it has expansion frames, the main frame can have only 1 AMP or 1AMP + sb AMP
Frame

## Slide 75
Common
Audio
Control
Timer
Others
04F
08F
16F
08/16F SS Exp
Deference
If different sound sources must be broadcast simultaneously to more than two zones, VX-3004F is required.
System detail
Difference between frames focused on audio route
VX-3004F
AMP
AMP
AMP
AMP
matrix
VX-3008F
AMP
AMP
SS
matrix
VX-3016F
AMP
SS
matrix
VX-3008F is necessary when the BGM of the other zone should not be stopped during the mic broadcasting to some zones.
If only one mic broadcast is performed, or when BGM in other zone can be stopped during mic broadcasting, 16F can be used.
These three types of selection are not only "selection of scale" but also "selection of functions". Please be careful in selecting the difference in function caused by the structure.
Frame

## Slide 76
AMP
System detail
AMP module
Class D
Module AMP unit, easy installation.
VX-015DA: 1ch, 150W VX-030DA: 1ch, 300W VX-050DA: 1ch, 500W
DC Power is supplied by VX-3000DS
for 50V, 70V, 100V line selectable
Sleep mode: makes the amplifier not engaged in broadcasting turned off, stopping the built-in fan operation.
1DS can be connected to Max 2,000W or 8ch
50V - 70V - 100V settings are
easily changed by this switch.
Even if you do not stop a system, can change AMP module just to turn off power of the applicable frame.
v.5.1

## Slide 77
SPline
System detail
Speaker line
2 wiring, 3 wiring, 4wiring
Hi-Z 50V, 70V, 100V line
High sensitive surveillance with EOL unit
@ VX-3004F
@ VX-3008F
VX-3016F
@ 3 wiring
@ 4 wiring

## Slide 78
System detail
Speaker line
2 wiring, 3 wiring, 4wiring
High sensitive surveillance with EOL unit
@ VX-3004F
@ VX-3008F
VX-3016F
@ 3 wiring
@ 4 wiring
Even when an attenuator is attached, it is possible to detect a fault in SP. When broadcasting is not being done, the system temporarily switches to emergency broadcasting to detect it.
The EOL unit is compatible with 2 wire or 4 wire type only. EOL unit can be attached to the system to which the attenuator is attached.
Hi-Z 50V, 70V, 100V line
SPline

## Slide 79
Hi-Z 50V, 70V, 100V line
System detail
Speaker line
2 wiring, 3 wiring, 4wiring
High sensitive surveillance with EOL unit
@ VX-3004F
@ VX-3008F
VX-3016F
@ 3 wiring
@ 4 wiring
SP
SP
ATT
N
R
C
Frame
H
ATTCONTROL
OUTPUT
SP
OUT
C
SP
OUT
H
SP
<General/BGM>
<Emergency>
With 3 wiring method, the SP line goes by way of a relay in the “ATTCONTROL OUTPUT” of Frame.
When a system activate the emergency mode, the system realizes a nullification of attenuator by changing the relay.
In the case of 4 wiring method, the DC line for ATT control goes by way of the “ATTCONTROL OUTPUT”. In most cases, DC 24V is used for the voltage.
ATT
N
R
C
Frame
H
ATTCONTROL
OUTPUT
SP
OUT
C
SP
OUT
H
SP
SPline

## Slide 80
System detail
General Microphone
RM-300X & RM-210F
Fireman’s Microphone
RM-200SF & RM-320F
This sheet first provides a rough introduction to the classification of RM.
The common feature is that they have keys that can be used not only for broadcasting floors, but also for various functions.
RM
This can be a hardware interface for emergency broadcasting. It has a "key to activate emergency broadcasts" and a high-priority microphone.
This is a microphone that is used a lot on a daily basis. This microphone can also make emergency broadcasts.
General Microphone
RM-500
This is also a microphone that is used a lot on a daily basis. What is inferior to the RM-300X is that it does not have an emergency broadcast function. On the other hand, its advantage is that it can be installed compactly because the functions of the keys can be switched using the LCD screen.
v.5.2

## Slide 81
System detail

## Slide 82
RM
System detail
These are possible configurable features set to mic’s function keys. However, the talk key dose not apply. The functions that can be set for this talk key are ON/OFF of MIC, or Mic ON/OFF with zone selection.
When set to
RM can have different priority when in General mode and in emergency mode.
Control Input
Emg RM key
Gen RM key
Notes: 表変更

## Slide 83
System detail
A small improvement
2) Chime
RM set for Emergency/General combined use can broadcast a chime at the time of general broadcast starting/ending.
1) Hybrid style
When the system is in general mode, the RM is operated with General priority,
other hand, when the system turn to EMG mode, the RM is operated as EMG microphone.
EMG
General

## Slide 84
System detail
Functions
which is activated by key
@* : Although the function names that can be set differ, the same function can be realized.
 |  | Frame |  | RM's key |  | RM-500 | RM-500 | PM
 |  | CI | Timer | Emg Emg/Gen | Gen | CI | Key | CI
General Bro. Pattern | Activate (level) | @ | @ | @* | @* | @ | @* | @
 | Activate (pulse) | @ |  | @* | @* | @ | @* | @
Base pattern | Activate | @ | @ | @ | @ |  | @ | @
 | Interrupt | @ | @ | @ | @ |  | @ | @
Volume Adjustment | Zone volume (level) | @ | @ |  |  |  |  | @
 | Zone volume (pulse) | @ | @ | @ | @ |  | @ | @
 | Input volume (level) | @ |  |  |  |  |  | @
 | Input volume (pulse) | @ |  | @ | @ |  | @ | @
Time adjustment |  | @ |  |  |  |  |  | @
Emergency Bro. Pattern | Start | @ |  | @ |  |  |  | 
 | Stop | @ |  | @ |  |  |  | 
 | Start and Stop | @ |  | @ |  |  |  | 
Emergency Sequence | Stop | @ |  | @ |  |  |  | 
 | Phase shift | @ |  | @ |  |  |  | 
Emergency Mode | Reset | @ |  | @ |  |  |  | 
 | Silence | @ |  | @ |  |  |  | 
 | EV Broadcast |  |  | @ |  |  |  | 
 | Acknowledge |  |  | @ |  |  |  | 
Emergency Warning Broadcast |  | @ |  | @ | @ | @ | @ | @
Malfunction | Fault Acknowledge | @ |  | @ | @ |  |  | 
 | Fault Reset | @ |  | @ | @ |  |  | 
 | External Fault Input | @ |  | @ | @ |  |  | 
Pre Select | Pattern |  |  | @ | @ |  | @ | 
 | Indovidual |  |  | @ | @ |  | @ | 
 | Clear |  |  | @ | @ |  | @ | 
Intended Control in/out | Input Operation |  |  | @ | @ |  | @ | 
 | Output Operation (level/pulse) |  | @ | @ | @ |  | @ | 
Maintenance | RM Broadcast Status |  |  | @ | @ |  | @ | 
 | Audio Monitor |  |  | @ | @ |  |  | 
 | Disablement of EMG control from CI |  |  | @ |  |  |  | 
 | Lamp Test |  |  | @ | @ |  |  | 
Power ON |  | @ | @ | @ | @ | @ | @ | @
Talk |  |  |  |  | @ |  | @ | 
Emergency Talk |  |  |  | @ |  |  |  | 
General Talk |  |  |  | @ |  |  |  | 
 |  | Frame |  | RM's key |  | RM-500 | RM-500 | PM
 |  | CI | Timer | Emg Emg/Gen | Gen | CI | Key | CI
General Bro. Pattern | Activate (level) | @ | @ | @* | @* | @ | @* | @
 | Activate (pulse) | @ |  | @* | @* | @ | @* | @
Base pattern | Activate | @ | @ | @ | @ |  | @ | @
 | Interrupt | @ | @ | @ | @ |  | @ | @
Volume Adjustment | Zone volume (level) | @ | @ |  |  |  |  | @
 | Zone volume (pulse) | @ | @ | @ | @ |  | @ | @
 | Input volume (level) | @ |  |  |  |  |  | @
 | Input volume (pulse) | @ |  | @ | @ |  | @ | @
Time adjustment |  | @ |  |  |  |  |  | @
Emergency Bro. Pattern | Start | @ |  | @ |  |  |  | 
 | Stop | @ |  | @ |  |  |  | 
 | Start and Stop | @ |  | @ |  |  |  | 
Emergency Sequence | Stop | @ |  | @ |  |  |  | 
 | Phase shift | @ |  | @ |  |  |  | 
Emergency Mode | Reset | @ |  | @ |  |  |  | 
 | Silence | @ |  | @ |  |  |  | 
 | EV Broadcast |  |  | @ |  |  |  | 
 | Acknowledge |  |  | @ |  |  |  | 
Emergency Warning Broadcast |  | @ |  | @ | @ | @ | @ | @
EV(General/BGM) Playback |  |  |  | @ | @ |  | @ | 
Malfunction | Fault Acknowledge | @ |  | @ | @ |  |  | 
 | Fault Reset | @ |  | @ | @ |  |  | 
 | External Fault Input | @ |  | @ | @ |  |  | 
Pre Select | Pattern |  |  | @ | @ |  | @ | 
 | Indovidual |  |  | @ | @ |  | @ | 
 | Clear |  |  | @ | @ |  | @ | 
Intended Control in/out | Input Operation |  |  | @ | @ |  | @ | 
 | Output Operation (level/pulse) |  | @ | @ | @ |  | @ | 
Maintenance | RM Broadcast Status |  |  | @ | @ |  | @ | 
 | Audio Monitor |  |  | @ | @ |  |  | 
 | Disablement of EMG control from CI |  |  | @ |  |  |  | 
 | Lamp Test |  |  | @ | @ |  |  | 
Power ON |  | @ | @ | @ | @ | @ | @ | @
Talk |  |  |  |  | @ |  | @ | 
Emergency Talk |  |  |  | @ |  |  |  | 
General Talk |  |  |  | @ |  |  |  | 

## Slide 85
Remote Microphone
RM-300X,210F and RM-200SF,320F
RM
System detail
Zone selection | 1st
Talk MIC on | 2nd
Spot CM from inside EV | 
Control output (pulse) to activate external EV | 
Talk finish | 4th
Zone addition | 3rd
Live announcement
& SPOT BGM
Emergency broadcast
General broadcast
(Fixed input/output)
General broadcast pattern activation Audio in 1 -> Zone 2 + Control out 2 | 1st
General broadcast pattern stop | 2nd
Base pattern 2 change EV 6 -> Zone 1-10 | 2nd
Base pattern 2 stop | 3rd
Base pattern 1 start EV 5 -> Zone 1-15 | 1st
Base pattern
(Entire BGM program)
Setting and Operation example
1st | Emg broadcast pattern start Auto alert announcement start
2nd | Sequence shift Change to evacuation announcement manually
 | Emg broadcast pattern stop
 | Spot live announcement and broadcast reset message
3rd | Emg reset Broadcast reset message and return to general mode
1st | 
2nd | 
Operation order
or
Assigned function

## Slide 86
System detail
RM
[0]-[9] key
These can also be used as numeric keys,
and can be assign functions.
[Chime] key
These keys are also responsible for ringing the chime, but they can also be assigned other functions.
Remote Microphone
RM-300X,210F and RM-200SF,320F
General Microphone
RM-500
PTT/Lock selectable
4 kind preset chimes
User’s original chimes
1ch AUX input
10 keys
General
v.5.2

## Slide 87
System detail
RM
Remote Microphone
RM-500
General Microphone
RM-500
PTT/Lock selectable
4 kind preset chimes
User’s original chimes
1ch AUX input
10 keys
General
@* : Although the function names that can be set differ, the same function can be realized.
Functions
which is activated by RM-500
 |  | Frame |  | RM's key |  | RM-500 | RM-500 | PM
 |  | CI | Timer | Emg Emg/Gen | Gen | CI | Key | CI
General Bro. Pattern | Activate (level) | @ | @ | @* | @* | @ | @* | @
 | Activate (pulse) | @ |  | @* | @* | @ | @* | @
Base pattern | Activate | @ | @ | @ | @ |  | @ | @
 | Interrupt | @ | @ | @ | @ |  | @ | @
Volume Adjustment | Zone volume (level) | @ | @ |  |  |  |  | @
 | Zone volume (pulse) | @ | @ | @ | @ |  | @ | @
 | Input volume (level) | @ |  |  |  |  |  | @
 | Input volume (pulse) | @ |  | @ | @ |  | @ | @
Time adjustment |  | @ |  |  |  |  |  | @
Emergency Bro. Pattern | Start | @ |  | @ |  |  |  | 
 | Stop | @ |  | @ |  |  |  | 
 | Start and Stop | @ |  | @ |  |  |  | 
Emergency Sequence | Stop | @ |  | @ |  |  |  | 
 | Phase shift | @ |  | @ |  |  |  | 
Emergency Mode | Reset | @ |  | @ |  |  |  | 
 | Silence | @ |  | @ |  |  |  | 
 | EV Broadcast |  |  | @ |  |  |  | 
 | Acknowledge |  |  | @ |  |  |  | 
Emergency Warning Broadcast |  | @ |  | @ | @ | @ | @ | @
EV(General/BGM) Playback |  |  |  | @ | @ |  | @ | 
Malfunction | Fault Acknowledge | @ |  | @ | @ |  |  | 
 | Fault Reset | @ |  | @ | @ |  |  | 
 | External Fault Input | @ |  | @ | @ |  |  | 
Pre Select | Pattern |  |  | @ | @ |  | @ | 
 | Indovidual |  |  | @ | @ |  | @ | 
 | Clear |  |  | @ | @ |  | @ | 
Intended Control in/out | Input Operation |  |  | @ | @ |  | @ | 
 | Output Operation (level/pulse) |  | @ | @ | @ |  | @ | 
Maintenance | RM Broadcast Status |  |  | @ | @ |  | @ | 
 | Audio Monitor |  |  | @ | @ |  |  | 
 | Disablement of EMG control from CI |  |  | @ |  |  |  | 
 | Lamp Test |  |  | @ | @ |  |  | 
Power ON |  | @ | @ | @ | @ | @ | @ | @
Talk |  |  |  |  | @ |  | @ | 
Emergency Talk |  |  |  | @ |  |  |  | 
General Talk |  |  |  | @ |  |  |  | 
v.5.2

## Slide 88
Remote Microphone
Common
RM
General Microphone
RM-300X & RM-210F
Fireman’s Microphone
RM-200SF & RM-320F
MAX: 7unit (70 keys) / 1unit RM-300X
EMG
EMG
General
PTT/Lock selectable
4 kind chimes
1ch AUX input
PTT/Lock selectable
4 kind chimes
MAX: 4unit (80 keys) / 1unit RM-200SF
System detail
MAX: 8units of RM / Frame
2 RS links (2ch) / 1unit Frame
Star wiring
daisy chain
Up to 8 Remote mic (RM) are connected to 1 frame. The RMs are connected by star wiring or daisy chain.
MAX: 4units of RM / 1 RS link
Basically, you can connect the Fire man’s MIC everywhere on the RS link. But EN54 requires that the Fire man’s MIC must be the first microphone connected to the main frame.
From v.3, Connecting more than one Fireman’s microphone to one line became possible.
RM-200RJ is used for wiring.
v.3
RS link A
RS link B
MAX: 320units of RM / System
320 = 8unit * 40 Frames

## Slide 89
RM
System detail
Power Supply
RS link
Up to 2 RMs, their power supply can be supplied from the frame via RS link.
If there are more RMs, they must be supplied from DS or AC adapter.
* Specifically, it determines whether it can be supplied from the frame by the current consumed by RM. Please refer to Installation Manual.
DS or AC adapter
Wiring Length
RS link
1) RM: 1 unit without expansion
2) RS link: φ1.2mm, 4-p shielded CPEV
3) Power: supplied from the frame
supplied with power from DS operated by AC power
max 1,200m
1) RM: 1 unit without expansion
2) RS link: STP Cat5
3) Power: supplied From the frame
supplied with power from DS operated by Battery
max 336m
Example
The wiring distance between the RM and the frame is determined by
1) the quantity of RM, 2) the RS link spec, 3) Power condition.
* In the Installation Manual, the maximum distance under some conditions is written.
Remote Microphone
Common

## Slide 90
System detail
PM

## Slide 91
System detail
PM
 |  |  |  |  |  | NW0 (same NW) | NW1,2 (other NW)
 |  |  |  |  |  | F | F
 |  | Input | Type | Unicast | Pattern |  | 
NW0 | PM | Audio input | General |  | General Broadcast | Possible | Impossible
 |  |  | BGM |  | General Broadcast | Possible | Impossible
 |  |  |  |  | Base | Possible | Impossible
 |  |  | EMG WRN |  | - | Possible | Impossible
 |  |  | General | X | General Broadcast | Possible | Possible
 |  |  | BGM | X | General Broadcast | Possible | Impossible
 |  |  |  |  | Base | Possible | Impossible
 |  |  | EMG WRN | X | - | Possible | Impossible
 | F | Audio input RM | -any- | - | -any- | Possible | Impossible
 |  | EV | General | - | General Broadcast | Possible | Possible
 |  |  | BGM | - | General Broadcast | Possible | Possible
 |  |  |  |  | Base | Possible | Possible
 |  |  | Alert/Evac Rest | - | Emergency Broadcast | Possible | Possible
Conditions for broadcasting
to different networks
The table on the left shows whether broadcasting is possible from PM and F (Frame) in NW0 to F in NW0, 1, and 2.
In the end, only the following two broadcasts can be broadcast across networks.
1) Signal which input from PM audio in
- However, the audio in is specified for unicast and must be set General type.
2) Frame EV (built-in sound source)
- However, EVs are not sent with unicast, but the EVs of one Frame in each NW are played back in conjunction.
Chime: Even if the PM’s Audio Input type is set to “General”, it cannot be accompanied by a chime.
Control Output: Control Output across multiple NWs can be activated as one control output pattern.

## Slide 92
System detail
PM
 |  |  |  |  |  | NW0 (same NW) | NW1,2 (other NW)
 |  |  |  |  |  | F | F
 |  | Input | Type | Unicast | Pattern |  | 
NW0 | PM | Audio input | General |  | General Broadcast | Possible | Impossible
 |  |  | BGM |  | General Broadcast | Possible | Impossible
 |  |  |  |  | Base | Possible | Impossible
 |  |  | EMG WRN |  | - | Possible | Impossible
 |  |  | General | X | General Broadcast | Possible | Possible
 |  |  | BGM | X | General Broadcast | Possible | Impossible
 |  |  |  |  | Base | Possible | Impossible
 |  |  | EMG WRN | X | - | Possible | Impossible
 | F | Audio input RM | -any- | - | -any- | Possible | Impossible
 |  | EV | General | - | General Broadcast | Possible | Possible
 |  |  | BGM | - | General Broadcast | Possible | Possible
 |  |  |  |  | Base | Possible | Possible
 |  |  | Alert/Evac Rest | - | Emergency Broadcast | Possible | Possible
Conditions for broadcasting
to different networks
The table on the left shows whether broadcasting is possible from PM and F (Frame) in NW0 to F in NW0, 1, and 2.
In the end, only the following two broadcasts can be broadcast across networks.
1) Signal which input from PM audio in
- However, the audio in is specified for unicast and must be set General type.
2) Frame EV (built-in sound source)
- However, EVs are not sent with unicast, but the EVs of one Frame in each NW are played back in conjunction.
Chime: Even if the PM’s Audio Input type is set to “General”, it cannot be accompanied by a chime.
Control Output: Control Output across multiple NWs can be activated as one control output pattern.
When broadcasting to different NWs, the PM audio input must be determined which NWs can be broadcast.
Up to 7 unicasts can be sent from one PM. The figure below shows some examples when the maximum number is set.

## Slide 93
VX link | 8ch | Audio input can be output to other frame via VX link
Unicast | 7ch | Audio input can be output to other frame in other network with Unicast communication.
PM
Audio | 8ch | Common spec VR on front panel, DSP: VOX only 1*-4ch *1ch on front 6.3mm, phone Balanced, Removable, * common input Gain: 0dB,-20dB,-40dB,-60dB selectable 5-6ch Unbalanced, Removable, Gain: -20dB 7-8ch Unbalanced, Removable, Gain: 0dB
Unicast | 7ch | Receives unicast broadcasts sent by PMs installed in other NWs.
Audio Input
Audio Output
VX link
The MIX function is the same as that of the frame.
See Frame Audio in this material. JUNP >>
System detail
Preamp Matrix Panel
VX link out 8ch
AUDIO IN 8ch
MIX
VX-3000PM
Matrix
VOX
Unicast out 7ch
VR
Unicast in 7ch

## Slide 94
Control | 10ch | 1-5ch Relay, WV: 30V DC, Current: 1A 6-10ch Open Collector, WV: 30V DC, Current: 100mA
PM
Control | 20ch | Non Voltage, OV: 30V DC, Current: 2-10mA
Control Input
Control Output
VX link
System detail
Preamp Matrix Panel
VX link out 8ch
AUDIO IN 8ch
MIX
VX-3000PM
Matrix
VOX
Unicast out 7ch
VR
Unicast in 7ch

## Slide 95
v.5.1
Control | 10ch | 1-5ch Relay, WV: 30V DC, Current: 1A 6-10ch Open Collector, WV: 30V DC, Current: 100mA
PM
Control | 20ch | Non Voltage, OV: 30V DC, Current: 2-10mA
Control Input
Control Output
VX link
System detail
Preamp Matrix Panel
VX link out 8ch
AUDIO IN 8ch
MIX
VX-3000PM
Matrix
VOX
Unicast out 7ch
VR
 |  | Frame |  | RM's key |  | RM-500 | RM-500 | PM | CT
 |  | CI | Timer | Emg Emg/Gen | Gen | CI | Key | CI | Key
General Bro. Pattern | Activate (level) | @ | @ | @* | @* | @ | @* | @ | 
 | Activate (pulse) | @ |  | @* | @* | @ | @* | @ | @
Base pattern | Activate | @ | @ | @ | @ |  | @ | @ | @
 | Interrupt | @ | @ | @ | @ |  | @ | @ | @
Volume Adjustment | Zone volume (level) | @ | @ |  |  |  |  | @ | 
 | Zone volume (pulse) | @ | @ | @ | @ |  | @ | @ | @
 | Input volume (level) | @ |  |  |  |  |  | @ | 
 | Input volume (pulse) | @ |  | @ | @ |  | @ | @ | @
Time adjustment |  | @ |  |  |  |  |  | @ | 
Emergency Bro. Pattern | Start | @ |  | @ |  |  |  |  | 
 | Stop | @ |  | @ |  |  |  |  | 
 | Start and Stop | @ |  | @ |  |  |  |  | 
Emergency Sequence | Stop | @ |  | @ |  |  |  |  | 
 | Phase shift | @ |  | @ |  |  |  |  | 
Emergency Mode | Reset | @ |  | @ |  |  |  |  | 
 | Silence | @ |  | @ |  |  |  |  | 
 | EV Broadcast |  |  | @ |  |  |  |  | 
 | Acknowledge |  |  | @ |  |  |  |  | 
Emergency Warning Broadcast |  | @ |  | @ | @ | @ | @ | @ | @
EV(General/BGM) Playback |  |  |  | @ | @ |  | @ |  | @
Malfunction | Fault Acknowledge | @ |  | @ | @ |  |  |  | 
 | Fault Reset | @ |  | @ | @ |  |  |  | 
 | External Fault Input | @ |  | @ | @ |  |  |  | 
Pre Select | Pattern |  |  | @ | @ |  | @ |  | @
 | Indovidual |  |  | @ | @ |  | @ |  | @
 | Clear |  |  | @ | @ |  | @ |  | @
Intended Control in/out | Input Operation |  |  | @ | @ |  | @ |  | @
 | Output Operation (level/pulse) |  | @ | @ | @ |  | @ |  | @
Maintenance | RM Broadcast Status |  |  | @ | @ |  | @ |  | 
 | Audio Monitor |  |  | @ | @ |  |  |  | 
 | Disablement of EMG control from CI |  |  | @ |  |  |  |  | 
 | Lamp Test |  |  | @ | @ |  |  |  | 
Power ON |  | @ | @ | @ | @ | @ | @ | @ | @
Talk |  |  |  |  | @ |  | @ |  | 
Emergency Talk |  |  |  | @ |  |  |  |  | 
General Talk |  |  |  | @ |  |  |  |  | 
NO/NC
NO/NC
These are possible configurable features. indicates that switching between normally open and normally closed is possible.
NO/NC
Control | 20ch | Non Voltage, OV: 30V DC, Current: 2-10mA
Control Input
Functions
which is activated by PM

## Slide 96
System detail
PM
When this function is drawn in detail so that you can understand the audio route, it looks like this.

## Slide 97
System detail
PM
AUDIO IN 8ch
MIX
VX-3000PM(0)
VOX
VXlink out 8ch
VR
In1
VX link
(NW 0)
AMP
AMP
AMP
AMP
matrix
Internal
EV
Frame(0)
All audio inputs of a PM are typically connected via VX links to frames within the network to which it belongs.
Matrix
When this function is drawn in detail so that you can understand the audio route, it looks like this.

## Slide 98
System detail
PM
AUDIO IN 8ch
MIX
VX-3000PM(0)
Matrix
VOX
Unicast out 7ch
VR
In1
Unicast communication is used here, so it can go beyond the router.
AMP
AMP
AMP
AMP
matrix
VX link
(NW 1)
VX link out 8ch
AUDIO IN 8ch
MIX
VX-3000PM(1)
Matrix
VOX
Unicast out 7ch
VR
Unicast in 7ch
Internal
EV
Frame(1)
PM(0) Audio In1 is configured for unicast communication
The broadcast is sent to the frame on the NW1 side via PM(1) on the NW1 side.
Multicast is sent within NW1 by PM(1) via VXlink(NW1).
PM can broadcast to 7 networks at the same time.
When a PM's audio input is configured for unicast communication,
that input becomes a dedicated input for connecting to PMs on other networks.

## Slide 99
System detail
PM
Unicast communication is used here, so it can go beyond the router.
AMP
AMP
AMP
AMP
matrix
VX link
(NW 1)
VX link out 8ch
AUDIO IN 8ch
MIX
VX-3000PM(1)
Matrix
VOX
Unicast out 7ch
VR
Unicast in 7ch
Internal
EV
Frame(1)
PM(0) Audio In1 is configured for unicast communication
The broadcast is sent to the frame on the NW1 side via PM(1) on the NW1 side.
Multicast is sent within NW1 by PM(1) via VXlink(NW1).
AMP
AMP
AMP
AMP
matrix
Internal
EV
Frame(0)
AUDIO IN 8ch
MIX
VX-3000PM(0)
VOX
Unicast out 7ch
VR
In1
VX link
(NW 0)
Matrix
It is possible to simultaneously broadcast unicast and multicast within the network(NW0) to which the PM(0) itself belongs.

## Slide 100
System detail
PM(0) Audio In1 is configured for unicast communication
AMP
AMP
AMP
AMP
matrix
Internal
EV
Frame(0)
impossible
PM
[Detail]
As you can see from this (in background) diagram,
PM does not have a VX link input.
In the configuration software GUI,
Zones belonging to different networks can belong to one Zone pattern, but if you select frame input as input in a broadcast pattern, etc., it will be displayed that broadcasting to Zones belonging to different NWs is not possible.
However, EV regeneration control is linked.
Even if PMs are connected by unicast, it is not possible to broadcast
from the Frame's "audio input" or "RM" to the Frame across different Networks.
However, if you select the built-in sound source (EV) as the input, EV will be broadcast to all Zones even if the pattern includes Zones belonging to different NWs. This is because each frame has exactly the same set of EVs. Only control information for playback is sent by unicast, and EVs are multicasted within each network.

## Slide 101
System detail
PM
AMP
AMP
AMP
matrix
Internal
EV
Frame(0)
LO
Act 2
Act 1
CO
Pattern
CO4
Zone:
Zone4(LO)
CO4
CI1
Broadcast Pattern
Zone
Patterns
Zone:
Frame(1) Zone1
Trigger
PM(0) CI 1
Audio input
PM(0) AI 1
General
If you want to broadcast live announcements from RM to Frame(1), two steps of activation will be required.
VX-3000PM(0)
Frame(0)
Frame(1)

## Slide 102
System detail
PM
AMP
AMP
AMP
matrix
Internal
EV
Frame(0)
LO
CO4
CI1
If you want to broadcast live announcements from RM to Frame(1), two steps of activation will be required.
VX-3000PM(0)
Frame(0)
Frame(1)
One unicast communication can be considered a single route. If multiple broadcasts are required simultaneously, the PM's multiple audio inputs must be configured for unicast.
PM(1)
PM(0)

## Slide 103
System detail
CT
Control Panel
VX link
 |  | Frame |  | RM's key |  | RM-500 | RM-500 | PM | CT
 |  | CI | Timer | Emg Emg/Gen | Gen | CI | Key | CI | Key
General Bro. Pattern | Activate (level) | @ | @ | @* | @* | @ | @* | @ | 
 | Activate (pulse) | @ |  | @* | @* | @ | @* | @ | @
Base pattern | Activate | @ | @ | @ | @ |  | @ | @ | @
 | Interrupt | @ | @ | @ | @ |  | @ | @ | @
Volume Adjustment | Zone volume (level) | @ | @ |  |  |  |  | @ | 
 | Zone volume (pulse) | @ | @ | @ | @ |  | @ | @ | @
 | Input volume (level) | @ |  |  |  |  |  | @ | 
 | Input volume (pulse) | @ |  | @ | @ |  | @ | @ | @
Time adjustment |  | @ |  |  |  |  |  | @ | 
Emergency Bro. Pattern | Start | @ |  | @ |  |  |  |  | 
 | Stop | @ |  | @ |  |  |  |  | 
 | Start and Stop | @ |  | @ |  |  |  |  | 
Emergency Sequence | Stop | @ |  | @ |  |  |  |  | 
 | Phase shift | @ |  | @ |  |  |  |  | 
Emergency Mode | Reset | @ |  | @ |  |  |  |  | 
 | Silence | @ |  | @ |  |  |  |  | 
 | EV Broadcast |  |  | @ |  |  |  |  | 
 | Acknowledge |  |  | @ |  |  |  |  | 
Emergency Warning Broadcast |  | @ |  | @ | @ | @ | @ | @ | @
EV(General/BGM) Playback |  |  |  | @ | @ |  | @ |  | @
Malfunction | Fault Acknowledge | @ |  | @ | @ |  |  |  | 
 | Fault Reset | @ |  | @ | @ |  |  |  | 
 | External Fault Input | @ |  | @ | @ |  |  |  | 
Pre Select | Pattern |  |  | @ | @ |  | @ |  | @
 | Indovidual |  |  | @ | @ |  | @ |  | @
 | Clear |  |  | @ | @ |  | @ |  | @
Intended Control in/out | Input Operation |  |  | @ | @ |  | @ |  | @
 | Output Operation (level/pulse) |  | @ | @ | @ |  | @ |  | @
Maintenance | RM Broadcast Status |  |  | @ | @ |  | @ |  | 
 | Audio Monitor |  |  | @ | @ |  |  |  | 
 | Disablement of EMG control from CI |  |  | @ |  |  |  |  | 
 | Lamp Test |  |  | @ | @ |  |  |  | 
Power ON |  | @ | @ | @ | @ | @ | @ | @ | @
Talk |  |  |  |  | @ |  | @ |  | 
Emergency Talk |  |  |  | @ |  |  |  |  | 
General Talk |  |  |  | @ |  |  |  |  | 
Functions
which is activated by CT
VX-3004F
AMP
AMP
AMP
AMP
matrix
VX-3008F
AMP
AMP
SS
matrix
VX-3016F
AMP
AMP
SS
matrix
Attenuation
The knobs allow you to attenuate the volume only for Frame’s audio input and Zone indicated by : -inf to 0dB.
Each knob can be assigned one audio input from every Frame or Zone in the system, even if they are located in multiple NWs.
However, the following cannot be assigned.
Frame: RM, EV and *Individual Zone of VX-3008 and 3016.
* In configuration software v.5.30 it appears to be assignable, but all Zones using the same AMP are attenuated.
PM: Audio input
If multiple knobs are assigned to the same Zone, the total value will be attenuated. Also, the sum of the knob value and the software setting value will be attenuated.
v.5.1

## Slide 104
DS
System detail
AMP
Battery
AMP
AMP
AMP
Max 25A, 8ch
Max 2,000W
Max 5A, 3ch
AC 220-230V
50/60W
DS link
(Max: 5m)
Power Distributer
DS has two kinds of power supply function.
AC power : 2ports * Both of these 2 ports must be connected to the power source
Battery : When a problem occurs in AC,
the system able to continue broadcast using Battery.
Both of these 2 ports must be connected to the power source.
Thease are not for backup.
Keeps a 2 x 12V sealed lead-acid battery charged while maintaining temperature compensation for the charging voltage.
Automatically disconnects the battery if its voltage reaches a discharge final level.
Recommended battery:
2 x Panasonic LC-X1265PG/APG
2 x Panasonic LC-XA12100P
2 x Panasonic LC-XB12100P*
2 x Yuasa NP65-12
2 x Yuasa NPL100-12
*Compliant with EN54-4
VX-3000DS
Frame
DS link
VX link
(Network)
AC 220-230V
50/60Hz
Battery
VX-3000DS
Frame

## Slide 105
DS
System detail
AMP
Battery
AMP
AMP
AMP
Max 25A, 8ch
Max 2,000W
Max 5A, 3ch
AMP
Battery
AMP
AMP
Max 5A, 3ch
AC 220-230V
50/60W
DS link
(Max: 5m)
Power Distributer
DS has two kinds of power supply function.
AC power : 2ports * Both of these 2 ports must be connected to the power source
Battery : When a problem occurs in AC,
the system able to continue broadcast using Battery.
Power have to be supplied individually for each AMPs and Frames. When there are 2 or more DS, DS link can be connected to other 3 DSs in the daisy chain. The trouble information of DS is sent to the Frame using this “DS link”. At least one “DS link” has to connect the DS and the Frame.
AC 220-230V
50/60W
Max 25A, 8ch
Max 2,000W
AMP
Battery
AMP
AMP
AMP
Max 5A, 3ch
Max 25A, 8ch
Max 2,000W
DS link
VX link
(Network)
AC 220-230V
50/60Hz
Battery
VX-3000DS
Frame

## Slide 106
Power have to be supplied individually for each AMPs and Frames. When there are 2 or more DS, DS link can be connected to other 3 DSs in the daisy chain. The trouble information of DS is sent to the Frame using this “DS link”. At least one “DS link” has to connect the DS and the Frame.
DS
System detail
VX-3000DS
AMP
Battery
AMP
AMP
AMP
Max 25A, 8ch
Max 2,000W
Max 5A, 3ch
AMP
Battery
AMP
AMP
Max 5A, 3ch
AC 220-230V
50/60W
DS link
AC 220-230V
50/60W
Power Distributer
DS has two kinds of power supply function.
AC power : 2ports * Both of these 2 ports must be connected to the power source
Battery : When a problem occurs in AC,
the system able to continue broadcast using Battery.
Frame
AMP
Battery
AMP
AMP
AMP
Max 5A, 3ch
Max 25A, 8ch
Max 2,000W
Max 25A, 8ch
Max 2,000W
AMP
AMP
AMP
AMP
AMP
AMP
AMP
AMP
Max 25A, 8ch
Max 2,000W
The limit to AMP connection of a DS
Satisfy both 2 following conditions.
8ch of AMPs or less
Total 2,000W or less
For an efficient design, please use a supplementary tool.
DS link
VX link
(Network)
AC 220-230V
50/60Hz
Battery
VX-3000DS
Frame

## Slide 107
DS link
VX link
(Network)
AC 220-230V
50/60Hz
Battery
VX-3000DS
Frame
DS
System detail
VX-3000DS
AMP
Battery
AMP
AMP
AMP
Max 25A, 8ch
Max 5A, 3ch
AMP
Battery
AMP
AMP
AMP
Max 25A, 8ch
Max 5A, 3ch
AC 220-230V
50/60W
DS link
AC 220-230V
50/60W
Power Distributer
DS has two kinds of power supply function.
AC power : 2ports * Both of these 2 ports must be connected to the power source
Battery : When a problem occurs in AC,
the system able to continue broadcast using Battery.
VX-3004F
AMP
Battery
AMP
AMP
AMP
Max 25A, 8ch
Max 5A, 3ch
Power have to be supplied individually for each AMPs and Frames.
When there are 2 or more DS, DS link can be connected to other DS in the daisy chain. The trouble information of DS is sent to the Frame using this “DS link”. At least one “DS link” has to connect the DS and the Frame.
VX link
When systems are located at several place, DS link is connected to Frame and DS at each setting place.

## Slide 108
VX link
System detail
VX link connection
VX link (Network)
Frame
Frame
Frame
B A
B A
B A
Setting
software
Each frames are connected with “VX link” which is IP network based.
Sound and control signal are streamed with this “VX link”.
There are 2 RJ45 ports of “VX link” on the frame. VX link supports duplication.
A method of connecting a single unit's LAN Link A and B terminals to each different switching hub to prevent the system from going down when a cable is broken or power fails.
Max 100m
Packet Size Changing
1024, 512, 256 byte
v.2
PC can be connected to either A or B
* PM and CT follow the same instructions as Frame.

## Slide 109
VX link
System detail
VX link connection
VX link (Network)
Frame
Frame
Frame
B A
B A
B A
Setting
software
Each frames are connected with “VX link” which is IP network based.
Sound and control signal are streamed with this “VX link”.
There are 2 RJ45 ports of “VX link” on the frame. VX link supports duplication.
Max 100m
Packet Size Changing
1024, 512, 256 byte
v.2
VX link can be connected into the daisy chain and the ring topology.
It is not necessary for you to set a spanning tree in SWHUB.
In addition, you can connect PC for setting to VX link directory.
* PM and CT follow the same instructions as Frame.

## Slide 110
VX link
System detail
VX link connection
VX link (Network)
Frame
Frame
Frame
B A
B A
B A
Setting
software
Each frames are connected with “VX link” which is IP network based.
Sound and control signal are streamed with this “VX link”.
There are 2 RJ45 ports of “VX link” on the frame. VX link supports duplication.
Max 100m
Packet Size Changing
1024, 512, 256 byte
v.2
VX link can be connected into the daisy chain and the ring topology.
It is not necessary for you to set a spanning tree in SWHUB.
In addition, you can connect PC for setting to VX link directory.
Ring topology and Duplex
VX link (Network)
Frame 01
Frame 00
Frame 02
B A
B A
B A
VX link (Network)
Frame 01
Frame 00
Frame 02
B A
B A
B A
X
A purple line is usually used for communication.
The system can continue communicating with a different route even if a problem happens in VX link between Frame 00 and 01.
The dualization of the communication line is realized by connecting VX link into the ring form with two ports comprised of each frame.
* PM and CT follow the same instructions as Frame.

## Slide 111
VX link
System detail
VX link connection
Each frames are connected with “VX link” which is IP based network.
Sound and control signal are streamed with this “VX link”.
There are 2 RJ45 ports of “VX link” on the frame. VX link supports duplication.
VX link can be connected into the daisy chain and the ring topology.
It is not necessary for you to set a spanning tree in SWHUB.
In addition, you can connect PC for setting to VX link directory.
VX link (Network)
Frame
Frame
Frame
B A
B A
B A
Setting
software
input 8ch
output 8ch
But HUBs must support
RSTP (Rapid Spanning Tree Protocol)
when external HUBs have
the ring topology, off course.
Frame
Frame
* PM and CT follow the same instructions as Frame.

## Slide 112
What should we think about Audio Link in VX link?
VX link
System detail
Audio route in VX link
This figure shows how the right VX-3004F receives audio signal from other frames via VX link. One VX-3004F can receive 4 BGMs and 4 others. Ultimately, these audio signals are input to the four outputs of the VX-3004F. The VX-3008F/30016F can receive a total of 4 audio signals. Because there are only 2 outputs.
All network routing and priority processing are automatically determined according to the broadcast pattern started.
.
AMP
AMP
AMP
AMP
matrix
VX link input 8ch
General/Emg./Emg.Warning: 4ch
BGM: 4ch
BGM is cut, mute* or mix* by/with General/Emergency broadcast
* VX-3004F only
BGM
BGM
BGM
BGM
VX link (Network)
Receiving
case
* For PM, only transmit 8ch.
* PM does not have a receiving function of VX link audio.

## Slide 113
System detail
Audio route in VX link
AMP
AMP
AMP
AMP
matrix
EV
General
BGM
BGM
General
VX link output 8ch
.
AMP
AMP
AMP
AMP
matrix
BGM
BGM
BGM
BGM
VX link (Network)
Receiving
case
Transmitting
case
VX link (Network)
VX link
Next is the case of broadcasting from the left VX-3004F to other frames.
A total of 8 audio signals can be sent to different frames.
This number is the same for VX-3008F and VX-3016F.
What should we think about Audio Link in VX link?
* For PM, only transmit 8ch.
* PM does not have a receiving function of VX link audio.

## Slide 114
The result is very simple. All inputs and outputs of 4 frames form a matrix structure.
System detail
Audio route in VX link <Detail>
VX link
VX-3004F (1) VX-3004F (2) VX-3008F VX-3016F
1 - 16
1 2 3 4
1 - 8
Audio in
Audio in
Audio in
Audio in
Output 1 2 3 4
Input
VX-3004F (1)
VX-3004F (2)
VX-3008F
VX-3016F
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
When considering [Matrix in VX-30##F] and [VX link] together,
how is that audio routing drawn??
Specifically, when two VX-3004Fs, one VX-3008F and one VX-3016F are connected by VX link,
How is the audio route of the whole system including analog and network drawn?
Please be aware that the division by SS is outside the Matrix that VX link constitutes.
If you can accept this result, that does not matter. But if it is difficult, let me explain from the next page.
Although Inside EV is omitted, It is the same structure as Audio in.

## Slide 115
System detail
Audio in
Audio in
Audio in
Audio in
Output 1 2 3 4
VX-3004F (1)
VX-3004F(1)
Inside
Matrix
Input
VX-3004F (1)
Let's start with only one VX-3004F(1).
As I have already introduced, the VX-3004F has 2 RF links (RM route) and 4 Audio inputs, and these and 4 Outputs constitute a matrix.
(The internal EV is omitted.)
This is very easy. Let's name this matrix “Inside Matrix”.

## Slide 116
System detail
Input
VX-3004F (2)
This also applies to (2).
VX-3004F (2)
1 2 3 4
Audio in
Audio in
Audio in
Audio in
VX-3004F(2)
Inside
Matrix

## Slide 117
System detail
Audio in
Audio in
Audio in
Audio in
Output 1 2 3 4
VX-3004F (1)
VX-3004F(1)
Inside
Matrix
Input
VX-3004F (1)
Let's consider the situation where VX-3004 (1) and (2) are connected by VX link.
(1) can broadcast to the output of (2) via VX link.
VX-3004F (2)
1 2 3 4
VX link
(1)
(2)
VX link
VX link
VX-3004F(2)
Inside
Matrix
VX link
VX link
Outside
Matrix
This is not hardware, but it looks like Matrix.
Let's name it here
“VX link: Outside Matrix”.

## Slide 118
System detail
Audio in
Audio in
Audio in
Audio in
Output 1 2 3 4
VX-3004F (1)
VX-3004F(1)
Inside
Matrix
Input
VX-3004F (1)
Let's consider the situation where VX-3004 (1) and (2) are connected by VX link.
(1) can broadcast to the output of (2) via VX link.
VX-3004F (2)
1 2 3 4
VX link
(1)
(2)
VX link
VX link
VX-3004F(2)
Inside
Matrix
VX link
VX link
Outside
Matrix
This is not hardware, but it looks like Matrix.
Let's name it here
“VX link: Outside Matrix”.
1
2
A
B
1
2
A B
The reason why this "VX link: Outside Matrix" can be drawn as a Matrix structure is as follows:
"It is free to connect 1, 2 and A, B as shown on the left side" and "turn on Matrix cross point as shown on the right“, Theas are structurally the same.

## Slide 119
System detail
Audio in
Audio in
Audio in
Audio in
Output 1 2 3 4
VX-3004F (1)
VX-3004F(1)
Inside
Matrix
Input
VX-3004F (1)
(2) can also broadcast to (1) via VX link.
VX-3004F (2)
1 2 3 4
VX link
(1)
(2)
VX link
VX link
VX link
Outside
Matrix
Audio in
Audio in
Audio in
Audio in
VX-3004F(2)
Inside
Matrix
VX-3004F (2)
VX link
VX link
Outside
Matrix
There is
“VX link: Outside Matrix” too
In other words, when two frames are connected, each has two internal Matrix, but there are also two Matrix constituted by VX link in addition.
However, there is not much meaning to distinguish between these two types of Matrix. You can think of it as one big Matrix.

## Slide 120
Expanding this to 4 frames, it looks like this.
System detail
VX link
VX-3004F (1) VX-3004F (2) VX-3008F VX-3016F
1 - 16
1 2 3 4
1 - 8
Audio in
Audio in
Audio in
Audio in
Output 1 2 3 4
Input
VX-3004F (1)
VX-3004F (2)
VX-3008F
VX-3016F
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
Specifically, when two VX-3004Fs, one VX-3008F and one VX-3016F are connected by VX link,
How is the audio route of the whole system including analog and network drawn?
Please be aware that the division by SS is outside the Matrix that VX link constitutes.
When considering [Matrix in VX-30##F] and [VX link] together,
how is that audio routing drawn??
Audio route in VX link <Detail>

## Slide 121
When considering [Matrix in VX-30##F] and [VX link] together,
how is that audio routing drawn??
System detail
Audio route in VX link
VX link
VX-3004F (1) VX-3004F (2) VX-3008F VX-3016F
1 - 16
1 2 3 4
1 - 8
Audio in
Audio in
Audio in
Audio in
Output 1 2 3 4
Input
VX-3004F (1)
VX-3004F (2)
VX-3008F
VX-3016F
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
Audio in
Specifically, when two VX-3004Fs, one VX-3008F and one VX-3016F are connected by VX link,
How is the audio route of the whole system including analog and network drawn?
AMP
On earth how many broadcast is produced at the same time?
You should think about this elucidation in this way.
When MIC(or audio input, inside EV) and one set of AMP are connected,
it can be counted as one broadcasts.
Please imagine one big Matrix.
In the total number of the inputs and outputs, the little one is the answers.
In the 40 frames, there are 240 inputs, and 160 AMPs (the number of AMP is the same as the number of the bus in the one frame),
so “160” is the answer.

## Slide 122
VX link
System detail
VX link Limitations and Notes
There are some restrictions on VX link connection.
1: SW HUB cascade level: Up to 7-level
2: Number of receiving stream /1frame: Up to 64 stream
3: Communication capacity
Frame
Frame
Frame
B A
B A
B A
Frame
Frame
Frame
B A
B A
B A
Frame
B A
1
2
3
4
5
6
Frame
7
B A
The number of the “level” from the frame of the origin of transmission to a reception frame must be less than up to 7.
The “level” is counted for 1 between frames.
Frame
B A
3
Frame
B A
1
2
The “level” is counted for 1 between frame-HUB, HUB-HUB.
2
Frame
01
Frame
00
Frame
02
Frame
04
Frame
03
Frame
05
Frame
06
Frame
07
Frame
08
Frame
09
1
2
3
You can connect more than 8 frames (up to 40 frames) using SW HUB in star topology.
The number of hops from the frame 00 is
2 level : to the frame 01 – 04
3 level : to the frame 05 – 09

## Slide 123
VX link
System detail
VX link Limitations and Notes
There are some restrictions on VX link connection.
1: SW HUB cascade level: Up to 7-level
2: Number of receiving stream /1frame: Up to 64 stream
3: Communication capacity
Frame
Frame
Frame
B A
B A
B A
Frame
Frame
Frame
B A
B A
B A
Frame
B A
1
2
3
4
5
6
Frame
7
B A
The number of the “level” from the frame of the origin of transmission to a reception frame must be less than up to 7.
The “level” is counted for 1 between frames.
Frame
B A
3
Frame
B A
1
2
The “level” is counted for 1 between frame-HUB, HUB-HUB.
2
Frame
01
Frame
00
Frame
02
Frame
04
Frame
03
Frame
05
Frame
06
Frame
07
Frame
08
Frame
09
1
2
3
You can connect more than 8 frames (up to 40 frames) using SW HUB in star topology.
The number of hops from the frame 00 is
2 level : to the frame 01 – 04
3 level : to the frame 05 – 09

## Slide 124
VX link
System detail
VX link uses multicast to communicate. In multicast, a single frame receives all existing streams. The stream that the frame should not be broadcasted is received once in that frame and then discarded. Due to the load of this discard processing, one frame should not receive more than 64 streams. (If 64 or more are received, the sound may become intermittent.)
Frame
Frame
Frame
Frame
Frame
Frame
Frame
Frame
Up to 64
stream
This means that no more than 8 frames should be connected to one SW HUB. This is because one frame transmits 8 streams.
64 stream
8 Frames
64 stream
8 Frames
64 stream
8 Frames
When connecting more than 9 frames,
Use SWHUB with IGMP snooping function. This is a function that sends only the stream that the Frame has requested to receive and broadcast to SP.
Limit the number of frames connected to the HUB to 8 or less. As a result, the number of streams required by frames below the hub can be kept below 64.
The effects of (1) and (2) prevent receiving more than 64 streams in one frame.
VX link Limitations and Notes
There are some restrictions on VX link connection.
1: SW HUB cascade level: Up to 7-level
2: Number of receiving stream /1frame: Up to 64 stream
3: Communication capacity

## Slide 125
VX link
System detail
This is a basic consideration in network design.
When communication is performed as shown in the figure below, 128 streams are transmitted over the main line. As a safe guide, 1 Mbps per stream is required for VX-link. In this case, 128Mbps is required for the trunk line.
64 stream
8 Frames
64 stream
8 Frames
The VX-3000 system basically requires 100BASE-TX, but please request a network design that can communicate with sufficient capacity according to the communication capacity.
64 stream
8 Frames
64 stream
8 Frames
Trunk line
128 stream
VX link Limitations and Notes
There are some restrictions on VX link connection.
1: SW HUB cascade level: Up to 7-level
2: Number of receiving stream /1frame: Up to 64 stream
3: Communication capacity

## Slide 126
v.4
adv
4 Systems Integration
System detail
4sys
Integ.
System 3
Max 40 frames
Max 240 inputs
Max 640 outputs
etc...
System 4
Max 40 frames
Max 240 inputs
Max 640 outputs
etc...
System 1
Max 40 frames
Max 240 inputs
Max 640 outputs
etc...
System 2
Max 40 frames
Max 240 inputs
Max 640 outputs
etc...
32 ->
32 ->
<-32
<-32
VX link
It is possible to integrate the 4 systems via VX link and constitute 1 large system.
A single system can receive up to 32 streams (broadcasts) from other systems.

## Slide 127
v.4
adv
4 Systems Integration
32 in
32 in
32 in
32 in
System detail
4sys
Integ.
One system can output 96 streams (broadcasts) and receive 32 streams (broadcasts).
In the total of 4 systems, a matrix like the one on the left is constructed.
System 1
Max 40 frames
System 2
Max 40 frames
System 3
Max 40 frames
System 4
Max 40 frames
System 1
Max 40 frames
System 4
Max 40 frames
32
Output
4 SP out x40
96 out to other system (32 out/to 1 system)
Input
4 Audio in
2 RM in (RS link) x40
4 Insted EV
32 in from other system
32 out
32 out
32 out
32 out
32 out
32 out
32 out
32 out
32 out
32 out
32 out
32 out
System 1
Max 40 frames
System 3
Max 40 frames
System 2
Max 40 frames
System 4
Max 40 frames
One system shown on the right figure is a matrix composed of 40 frames: (400 + 32) in x (160 + 96) out at max.
System
Max 40 frames
32 x 32 matrix
The connection between each system is shown in the figure below in detail.
System 3
Max 40 frames
32
System 2
Max 40 frames
32

## Slide 128
System detail
4sys
Integ.
Available functions
Other System
Own System
General Broadcast Pattern
Zone
Patterns
Zone
CO
Patterns
CO
CO
Zone
Single Audio input
・RM’s AUX input
・Frame’s audio input
・Frame’s inside EV
BGM
General
Type
Emergency Broadcast Pattern
Zone
Pattern
Zone
Zone
CO
Pattern
CO
CO
Emergency sequence
EV1
EV2
EV3
Zone
Zone
CO
CO
Zone
Zone
CO
CO
Zone
Patterns
Zone
Zone
CO
Patterns
CO
CO
The zone pattern, control output pattern, fault detection items set in other system can be used in its own system.
The Own system allows General Broadcast in the zone of the Other system.
Emg. Broadcast also runs the Own System sequence in the Other System.
The Failure Output Patterns of other systems are available.
Failure Output Pattern
Detection Items
Analog Link, VX link,
DC power, DS-LINK,
AMP, RM, Control input, External equipment,
Speaker line
Indicators (assignable)
Control Output
RM’s key indicator
E-mail
Failure Output Pattern
Detection Items
Analog Link, VX link,
DC power, DS-LINK,
AMP, RM, Control input, External equipment,
Speaker line
Indicators (assignable)
Control Output
RM’s key indicator
E-mail
v.4
adv
4 Systems Integration

## Slide 129
Failure Output Pattern
Detection Items
Analog Link, VX link,
DC power, DS-LINK,
AMP, RM, Control input, External equipment,
Speaker line
Indicators (assignable)
Control Output
RM’s key indicator
E-mail
System detail
4sys
Integ.
Other System
Own System
General Broadest Pattern
Zone
Patterns
Zone
CO
Patterns
CO
CO
Zone
Single Audio input
・RM’s AUX input
・Frame’s audio input
・Frame’s inside EV
BGM
General
Type
Emergency Broadcast Pattern
Zone
Pattern
Zone
Zone
CO
Pattern
CO
CO
Emergency sequence
EV1
EV2
EV3
Zone
Zone
CO
CO
Zone
Zone
CO
CO
It is not possible to set the EV (build-in WAV file) of the Other system to the event or pattern of the Own system.
EV
Base Pattern
Zone
Patterns
Zone
CO
Patterns
CO
CO
Zone
Single Audio input
・RM’s AUX input
・Frame’s audio input
・Frame’s inside EV
BGM
Type
Zone
Patterns
Zone
Zone
Zone
Impossible!
Impossible!
Impossible!
It is not possible to set the individual zone of the Other system to the event or pattern of the Own system.
It is not possible to set the zone pattern of the Other system to the Base pattern of the Own system.
Detection Items
Analog Link, VX link,
DC power, DS-LINK,
AMP, RM, Control input, External equipment,
Speaker line
Detection items of the Other systems can not be used.
Impossible!
Unavailable functions
There are some restrictions on this integrated system.
v.4
adv
4 Systems Integration

## Slide 130
System detail
4sys
Integ.
Other System
Frame
Own System
Frame
B A
B A
Impossible!
VX link
The Own system and The Other system can not be connected directly via VX link. SwHUB is required.
Other System
DS
Own System
DS
Impossible!
DS link
Own System
Frame
Impossible!
The Own system and The Other system can not be connected directly via DS link. It must be separated. Also the Own system can not be powered from the DS of the Other system.
Other System
Frame
Own System
Frame
Impossible!
100V line
sb AMP
Also, the Own system can not use Standby AMP of other system.
Other System
Frame
Own System
Frame
BGM
General
Only MIX
When broadcasting to Other system, General and BGM will be Mixed. Mute and Cut are invalid.
Between different systems are communicated by each ID: 0 frame. Even if there is a physical connection between the other frames, if there is a problem in communication between ID: 0, any operation that crosses the system can not be performed.
Other System
Frame ID:0
Own System
Frame ID:0
Frame ID:1
Frame ID:1
Frame ID:2
Frame ID:2
Necessary
Unavailable functions
There are some restrictions on this integrated system.
v.4
adv
4 Systems Integration
It is not possible to set up and maintain multiple systems with one GUI (screen). Setting and maintenance are possible with one PC,
but it would be realistic for a huge system to be split- managed.

## Slide 131
MIC
SS
SS
System Example
Office Building
It is not so big an office building. Broadcasting using a microphone is hardly done. BGM is always playback in public spaces such as lobby or cafe.
VX-3016F is selected for broadcasting in each office. This is because daily mic broadcasting will not be done, so it is sufficient to branch one audio route with SS. VX-3008F is selected for public areas such as lobby and cafe where BGM is necessary.
The difference between VX-3016F and 3008F is whether it is the single route or the double routes between the Admin room – the SS.
Public Spaces
needed BGM
AMP
AMP
sbAMP
SS
AMP
sb AMP
SS
Each Office
BGM
matrix
matrix
Admin room
Zone 1
AMP
AMP
Zone 2
Zone 1
AMP
Zone 2
BGM
MIC
BGM
MIC
SS
SS
Zone 1
AMP
AMP
Zone 2
Zone 1
AMP
Zone 2
BGM
MIC
BGM
In the case of a single route such as 3016F, if mic broadcasting is performed only to Zone 1, the system has no other way than to abruptly stop the BGM of Zone 2.
When using VX-3008F, the system can broadcast from mic to Zone 1, and Zone 2 can continue BGM broadcasting at the same time due to the double route structure.

## Slide 132
System Example
Several Mansions
matrix
SS
AMP
sb AMP
matrix
SS
32F
17F
16F
1F
There are several high-rise residences. SP is installed only in the corridor. There are not many SPs on each floor. There is no need to broadcast more than one at the same time, and there is no need for BGM. Broadcasting is done independently in each building, but simultaneous broadcasting to all buildings is also necessary.
Since multi-route broadcasting is unnecessary, VX-3016F which are SS-expanded is selected for each building.
Each VX-3016F is connected with VX link, and it can also broadcast to all building.
VX-3016F
VX-3016F

## Slide 133
System Example
BGM system
This is somewhat unusual usage as a PA system. This is the BGM system of facilities with many small rooms such as hotel SPA and gym. Each room has a switch and attenuator, user can select two types of BGM and adjust the volume. Normally, mixers are used for these systems, but if there are too many rooms VX-3008F (or 3016F) may be useful. In the event of a fire VX-3000 system can immediately turn to its original behavior.
Each room can independently select two BGMs because the VX-3008 has two routes that are completely separated. This can not be done when VX-3016F is used.
BGM A
AMP
AMP
sbAMP
SS
matrix
SS
matrix
Room 16
Room 09
Room 08
Room 01
BGM B
BGM A
BGM B
Room 01
BGM A
BGM B
Room 02
BGM A
BGM B
Room 03
BGM A
BGM B
Room 04
BGM A
BGM B
Room 05
BGM A
BGM B
Room 06
BGM A
BGM B
Room 07
BGM A
BGM B
Room 09
BGM A
BGM B
Room 10
BGM A
BGM B
Room 11
BGM A
BGM B
Room 12
BGM A
BGM B
Room 13
BGM A
BGM B
Room 14
BGM A
BGM B
Room 15
BGM A
BGM B
Room1
General Broadest Pattern
Room 01
BGM A
A01
General Broadest Pattern
Room 02
BGM2
B01
BGM A
BGM B
Room2
General Broadest Pattern
Room 02
BGM A
A02
General Broadest Pattern
Room 02
BGM B
B02
Connect an alternative switch to Control in and activate the General Broadcast pattern. When Pattern A02 is activated while BGM A is being broadcast to Room 01 by Pattern A01 activation, BGM A is also broadcasted to Room 02. When Pattern B02 is activated instead of Pattern A02 with Switch in Room 02, BGM B will be broadcast to Room 02. At this time, broadcasting of BGM A by pattern A01 continues in Room 01.

## Slide 134
System Example

## Slide 135
System Example
TOA's VX-3000 Series got certified with EN 50121-4 (IEC62236-4),
the electromagnetic standards which applies to a signaling and telecommunication apparatus installed in railway environment. Those systems can now be utilized in railway applications where EN 50121-4 is required.
EN 50121-4 specifies limits for emission and immunity and provides performance
criteria for signalling and telecommunications apparatus which may interfere
with other apparatus in the railway environment, or increase the total
emissions for the railway environment beyond the limits defined in the
appropriate standard and so risk causing electromagnetic interference to
apparatus outside the railway system.
Station
OCS
Station
Not only VX-3000 series, but also NX-300: Network Audio Adapter which connect OCS and Stations, EC-380: MIC got certified with

## Slide 136
System Example
Airport
The airport's broadcasting system is the system with the most input devices and output area. Input devices are multi-route auto announce machine, gates and information center mic, intercom etc. The output area is departure, arrival, boarding gate, shopping area, backyard, office etc. Although not detailed in this document, it is easy to imagine that it will be composed of many VX-3004F.
On this page, only one system interpretation is introduced. Although it is the boarding gate that many mics are installed, the areas they must broadcast are limited to the areas near the gate, there is no need to broadcast to all areas. In such a case, instead of recognizing the VX-3000 system as a large matrix, it is one measure to divide it into a global matrix and several local matrixes.
1 2 3 4
5 6 7 8
Auto
Announcer
9 10 11 12
Departure Gates
Auto
Announcer
Departure Gates
1 2 3 4
5 6 7 8
9 10 11 12
Departure Area Departure Area Departure Area
Departure Gates
Departure Gates
Same
Local Matrix
Global Matrix
only
only
only
Note that this is a difference in system recognition method, the specification of the system does not change, and the number of simultaneous broadcasts does not change either.
Broadcasting area
in boarding area

## Slide 137
System Example
Airport
The super huge airport is made up of several airport facilities. At these airports, there are occasions when it is not enough for 320 mics, 160 audio routes, or 640 Zone. In such a case, multiple VX-3000 can be connected by the customized IP-3000 system.
Also, this is not only a large system scale, it is also the best way to make partial maintenance possible.

## Slide 138
Thank you

## Slide 139
Frame
VX-3004F
System detail
Other variation
AMP
AMP
AMP
AMP
matrix
Max 4 AMP – 4 AB Zone
AMP
AMP
AMP
Max 3 AMP – 3 AB Zone & 1sbAMP
X
sb AMP
matrix
or
AMP
matrix
AMP
matrix
sbAMP
AMP
matrix
AMP
AMP
matrix
AMP
AMP
VX-3004F has multi-route structure. Each zone has exclusive AMP.
Up to 4 different source can be broadcasted to 4 different zones.
Close
with AMP

## Slide 140
Frame
VX-3004F
System detail
Other variation
AMP
AMP
AMP
AMP
matrix
Max 4 AMP – 4 AB Zone
AMP
AMP
AMP
Max 3 AMP – 3 AB Zone & 1sbAMP
X
sb AMP
matrix
or
AMP
matrix
AMP
matrix
sbAMP
AMP
matrix
AMP
AMP
matrix
AMP
AMP
VX-3004F has multi-route structure. Each zone has exclusive AMP.
Up to 4 different source can be broadcasted to 4 different zones.
Close

## Slide 141
Frame
System detail
Setting A
Setting B
Setting C
AMP
AMP
sbAMP
matrix
Max 2AMP – 8 Zone & 1sbAMP
SS
AMP
SS
AMP
Covered by
AMP
AMP
AMP
SS
AMP
Covered by
AMP
AMP
Covered by
AMP
SS
AMP
Covered by
AMP
AMP
Covered by
Covered by
AMP
AMP
equipped with 2in/8out speaker selector
You can arrange the zones which these two AMPs cover.
VX-3008F
VX-3008F has 2 bus line and 8 zone speaker selector. Using speaker selector, the system can broadcasts to many zones with only 1 AMP.
Appearance
Close

## Slide 142
Frame
System detail
AMP
AMP
matrix
Max 2 AMP – 16 Zone
SS
AMP
Max 1 AMP – 16 Zone & 1 standby AMP
X
sb AMP
matrix
SS
VX-3016F
VX-3016F has 2 bus line and 16 zone speaker selector. Using speaker selector, the system can broadcasts to many zones with only 1 AMP.
or
Close

## Slide 143
Update history
2016.10.15 Hiramatsu
-07 add about ID:0
-18 add about Analog link Max 800m
-21 add about redundant of ID:0 is impossible
-32 add variation of F04 configuration
-46 add limitations of RM connection
-48 add DS link max 5m
-51 add about the Star topology
-51 add LAN max 100m
-55 modified the number of HOP
2017.02.27
-12etc modified matrix figure
2017.03.21 modified RM’s number : RM-200F -> RM-200SF, RM-210M -> RM-320F
2017.04.18 add v.2 functions
2017.09 modified EV’s specification
2017.12.21 modified DS’s backup function and add DS’s function, recommended battery
2017.12.25 The relationship between ATT and SP surveillance was added
2018.02.19 Add v.3 functions and system example
2018.05.15 Modified number of “Emg Sequence” 4 -> 32
2018.06.04 Add v.4 functions
2018.07.18 Added explanation about RM
2019.09.24 Add v.5 functions
2019.11.22 Add VX link condition
2019.12.05 ANC parameter, EN 50121-4
2023.09.20 v.5.1 add PM, CT, LO, RM-500
2023.10.20 There was a mistake in drawing the battery connection diagram.
---------> 50/60Hz
Correct fig from VX-3000 Manual 133-02-00037-05
Mistake
on Rev. 20230922 1550 PS LV 220ppi
sheet 104-107